## A-Steam Power Stations
REPORT DATE -3 DECEMBER 2003
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 1 | 0 | 0 | 0 | 8 |  |  | 8 | 24 | No.1 loss of flame. No. 3 boiler leak. No. 2 stopped at 0053 FWP.
Baiji | Fuel Oil | 6 | 5 | 100 | 75 | 90 | 85 | 0 | 85 | 435 | 500 | No. 5 rehab.
Dura | Fuel Oil | 4 | 1 |  |  | 75 | 0 | 0 | 0 | 75 | 180 | No. 4: Programmed Maintenance 10 OCT to 25 NOV. Nos. 5 & 6: Rehabilitation.
South Baghdad | Fuel Oil | 6 | 3 | 35 | 25 | 0 | 35 | 0 | 0 | 95 | 200 | No. 6 programmed mnt 11 NOV to 26 DEC. No. 5 boiler leak. No. 3 boiler leak.
Mussaibe | Crude and Fuel Oil | 4 | 3 | 210 | 100 | 0 | 220 |  |  | 530 | 860 | No. 2 synch 1423. No. 3 program mnt 5 NOV to 20 DEC.
Nassirya | Crude | 4 | 3 | 150 | 150 | 0 | 100 |  |  | 400 | 600 | No. 3 programmed mnt 11 NOV to 11 DEC.
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 0 | 85 |  | 85 | 160 | No. 4 programmed mnt 6 NOV to 21 DEC.
Hartha | Natural Gas and Crude | 4 | 1 | 150 |  |  | 0 |  |  | 150 | 300 | No. 4 Programmed Maintenance from 23 OCT to 23 DEC.
[9 empty] | Total: | 1778 | 2824

## B- Gas_C-Power Stations
Report Date- 3 DECEMBER 2003
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 110 | 125 | Gas Oil | No. 2 problem in lube system. | Musil Dam Main | 4 | 2 | 180 | 600
Quds | 2 | 2 | 210 | 160 | Gas Oil | 40 trucks. | Musil Dam reg | 4 | 3 | 30 | 60 | 450
Mosil | 12 | 6 | 105 | 150 | 17 | No. 1 rotor defect. No. 2 ACC. No. 8 program mnt. No. 3 control cards. No. 4 vibration. No. 7 stopped 0806 vibration. | Musil Pumping | 2 | 0 | 0 | 0
Dibis | 3 | 0 | 0 | 60 | 20 | No. 5 problem turbine rotor. No. 6: Programmed Maintenance. No. 4 rotor defect. | Haditha Dam | 6 | 2 | 90 | 160 | 300
Old Mulla | 12 | 7 | 95 | 128 | 22 | No. 1 gas control. No. 2 gen protec. No. 5 Programmed Mnt. No. 12 rehab. No. 3 tripped HET. | Samarra | 3 | 2 | 40 | 55 | 550
New Mulla | 6 | 3 | 90 | 173 | 28 | No. 6 Generator Defective. No. 3 prog. Mnt. No. 1 EF. | Himrin | 2 | 1 | 18 | 21 | 75
Taji | 7 | 3 | 50 | 55 | 15 | No. 5 clutch. No.7 Rehabilitation. No. 2 look out gen. No. 4 stopped 1730 generator look out. | Hindia | 4 | 4 | 5 | 5 | 120
M. Taji | 2 | 0 | 0 | 20 | 0 | NGPL | Kufa | 4 | 0 | 0 | 1 | 60
Dura | 4 | 2 | 30 | 30 | 15 | No.3 Rehabilitation. No. 1 control. |  |  | Total | 363 | 896
Hilla | 4 | 4 | 65 | 64 | 24 |  | System Generation |  | 72282 | MWh
Najaf | 3 | 3 | 110 | 129 | 20 |  | Syrian Line Generation |  | 1382 | MWh
Khor | 4 | 1 | 30 | 80 | Natural Gas | No. 4: Rehabilitation. No. 1 vibration. No. 3 stopped 1235 fire in control | Turkey Line Generation |  | 1653 | MWh
Shuaiba | 2 | 1 | 10 | 20 | Natural Gas | No. 1 programmed mnt for 4 days. | Total Generation |  | 75317 | MWh
Petro | 4 | 0 | 0 | 0 | Natural Gas |  | System Peak Load |  | 3486 | MW
M. Dibis | 4 | 0 | 0 | 24 | Natural Gas |  | Syria Peak Load |  | 63 | MW
Mossil East | 5 | 0 | 0 | 15 | Gas Oil |  | Turkey Peak Load |  | 80 | MW
Hmam | 2 | 0 | 0 |  | Gas Oil |  | Fixed Gen Peak Load |  | 77 | MW
[7 empty] | Total Peak Load |  | 3706 | MW
|  | Total | 905 | 1233 |  |  | Baghdad Load |  | 1350 | MW
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
GOVERNORATE | Peak Load MW | MWH | Average Load MW | 3 DECEMBER, 2003
Baghdad | 1350 | 27016 | 1125.6667 | Power transferred from North to Middle 775 MW
Duhok | 80 | 1632 | 68
Naynawa | 315 | 5715 | 238.125 | Power transferred from South to Middle 160 MW
Tamim | 135 | 3240 | 135
Salah Aldeen | 215 | 4601 | 191.7083
Anbar | 205 | 3990 | 166.25
Dyala | 77 | 1714 | 71.4167
Babil | 105 | 2063 | 85.9583
Kirbala | 90 | 1252 | 52.1667
Najaf | 85 | 2030 | 84.5833
Kadsya | 70 | 1394 | 58.0833
Wasit | 100 | 2070 | 86.25
Muthana | 60 | 1403 | 58.4583
Nasirya | 110 | 2647 | 110.2917
Misan | 60 | 1443 | 60.125
Basra | 210 | 6078 | 253.25
3267