Power System Highlights for Monday, December 29, 2003

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Transmission Line Baghdad East – Kirkuk, 400Kv line repaired 1400 Dec 27, 2003. This link allows the network ability to transfer power from the North to the Center and Baghdad areas.

.

Generation:

- Daily System peak on 28 Dec – 3,832Mw.

- Daily system Demand on 28 Dec – 5,544 Mw (Estimated)

(3832, Actual Generation + 1378, Load Shed + 334, Corrected Frequency = 5544)

- Total generation – 81,171Mwh

- Imported power -  Power from Syria (20Mw) and Turkey (80Mw) included in System Peak

- Generators Returned to Service                                                       90 Mw

S. Baghdad 6 -------------------------------------------------------------------------35 Mw

S. Baghdad 4 -------------------------------------------------------------------------35 Mw

Taji 1 ------------------------------------------------------------------------------------15 Mw

- Generators Unscheduled Out of Service as of  28 DEC 03           742 Mw

Dibis 3 SP, tripped due to feed water pump problem ----------------------  8 Mw

* South Baghdad # 3, 12/28 Boiler Leak ------------------------------------- 35 Mw

* Daura 4, SP, Boiler Leak, 12/28 ---------------------------------------------  80 Mw

* Nassirya 4, 12/28, Maintenance----------------------------------------------130 Mw

Old Mulla 1,NG, Acc Gear --------------------------------------------------------15 Mw

Old Mulla 2, NG, Servo  and Circuit breaker problem ---------------------15 Mw

Old Mulla 4, NG, Vibration trip -------------------------------------------------- 15 Mw

Old Mulla 6, NG, Accessory Gear ----------------------------------------------15 Mw

New Mulla 6, NG, Generator Defect -----------------------------------------   30 Mw

Taji 3, NG, Compressor -----------------------------------------------------------15 Mw

Taji 4, NG, Turbine problem ------------------------------------------------------15 Mw

Taji 5, NG, Pilot Problem ----------------------------------------------------------15 Mw

Taji Mobile, NG, software problem ---------------------------------------------10 Mw

Baiji 2, NG, Insufficient Fuel ---------------------------------------------------- 100 Mw

Mosil 1, NG, Rotor Defect -------------------------------------------------------- 15 Mw

Mosil 2, NG, Servo problem ------------------------------------------------------15 Mw

Mosil 9, NG, Rotor Defect -------------------------------------------------------- 15 Mw

Shuaiba 1, NG, S/B -----------------------------------------------------------------10 Mw

Najebia 4 SP, Programmed maintenance complete, tripped 12/27----- 90 Mw

Najebia 5, SP, Lubricating oil leak ---------------------------------------------- 90 Mw

*  Dibis, 6 GP, 12/28, Synchronization -------------------------------------------9 Mw

RED – Denotes most recent out of service

- Generators Scheduled Out of Service as of 28 DEC 03                1071 Mw

- 2 Thermal units off-line for rehabilitation  ---------------------------------   200 Mw

  - Daura 5 and 6 – 200 Mw – ECD  May 2004

- 6 Thermal units in programmed maintenance --------------------------   623 Mw

  - Dibis 1 – 8 Mw –  ECD Jan 25

  - Baiji  6 -100 Mw –  ECD Jan 19

  - South Baghdad 5  35 Mw –  ECD Jan 15

  - Mussaibe 3          200 Mw – ECD Dec 21 (Not Complete yet)

  - Nassirya 3           130 Mw –  ECD Feb 04

  - Hartha 4               150 Mw – ECD Dec 23 (Not Complete yet)

- 6 Gas Turbine units off-line for rehabilitation ------------------------------123 Mw

  - Dibis 4, 5,          18 Mw

  - Old Mulla 12      15 Mw

  - Taji 7                 15 Mw

  - Daura 3             20 Mw

  - Khor Zubayr 4   55 Mw

- 5 Gas Turbine units in programmed maintenance------------------------125 Mw

  - Mosil 3                15 Mw

  - Old Mulla 5,7       30 Mw

  - New Mulla 5        30 Mw

  - Najaf 2                 50 Mw

Transmission:

Countrywide, Iraq’s electrical output continues to be constrained by damaged transmission and distribution lines. The lines have come down due to sabotage and bad weather.  Downed transmission lines increase the probability for complete nationwide blackout by reducing system contingency and causing mechanical damage at power plants. This may cause further temporary blackouts, which have already directly resulted in 1) impacted refineries causing reduced fuel flow to power plants and a subsequent reduction in power supply, and 2) damages in the power plants due to undercurrent causing units to come off-line for unscheduled maintenance.

- Transmission Lines out of service:

400KV

Haditha-Baghdad West –ECD slipped from Jan 24 to Feb 29

Haditha-Qarna – Wasit – ECD slipped from Jan 12 to Jan 24

Baghdad South – Qadisseya – ECD Jan 20

Baiji - Baghdad West #1 – ECD Jan 20

New line - Baghdad East-Baghdad South #2 – ECD Jan 23

Babil-Qadisiyah (collapsed towers/stolen conductors ECD 20 JAN)

Haditha – Qaim – no funding

Baiji – Haditha – no funding/no contractor

132KV

Mosul – Mosul East is sabotaged

Musalla – Rumala 132 Kv line still being sabotaged – 4 more towers down – now total of 7. This line ties the South generation to the North

Muthena GPS – Dour -  ECD Dec 28 ( No confirmation)

Shuwaiba-Toba-Hamar– ECD Dec 30, delay due to material shortage

Baghdad West – Faluja, tripped No ECD

Omara-Burzegan – Sabotaged. ECD March 2004

Lines Returned to service:

None reported today

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

NG:  NATURAL GAS

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

HYDRO:  WATER POWER