Power System Highlights for January 3, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Generation:

- Daily System peak on 2 Jan – 3,507Mw.

- Daily system Demand on 2 Jan – 5,491 Mw (Estimated)

(3507, Actual Generation + 1675, Load Shed + 309, Corrected Frequency = 5491)

- Total generation – 76,026Mwh

- Imported power -  Power from Syria (60Mw) and Turkey (80Mw) included in System Peak

- Generators Returned to Service  	               270 Mw

Baiji 1                                                                                                95 Mw

Baiji 4                                                                                                90 Mw

South Baghdad 2                                                                               25 Mw

Najebia 4                                                                                            30 Mw

Old Mulla 4                                                                                         15 Mw

Taji 6                                                                                                  15 Mw

- Generators Unscheduled Out of Service as of  2 JAN 04         791 Mw

Dibis 3 SP, tripped due to feed water pump problem ------------------  8 Mw

* Dibis 2 SP, Stopped 1523, gas valve problem ------------------------   8 Mw

* Baiji 2,  SP, Lack of HCL ---------------------------------------------------100 Mw

* Baiji 3, SP,  Boiler Leak ---------------------------------------------------- 100 Mw

Daura 4, 12/31, Bearings -----------------------------------------------------100 Mw

* Mussaibe2, SP, Seals -------------------------------------------------------200 Mw

* Najebia 5, Cooling Ejection Seals ----------------------------------------- 90 Mw

Mosil 1, NG, Rotor Defect ----------------------------------------------------- 15 Mw

Mosil 2, NG, Servo problem ---------------------------------------------------15 Mw

Mosil 9, NG, Rotor Defect ----------------------------------------------------- 15 Mw

Shuaiba 1, NG, S/B --------------------------------------------------------------10 Mw

Old Mulla 1,NG, Acc Gear -----------------------------------------------------15 Mw

Old Mulla 2, NG, Servo  and Circuit breaker problem ------------------ 15 Mw

Old Mulla 6, NG, Accessory Gear ------------------------------------------- 15 Mw

New Mulla 6, NG, Generator Defect ---------------------------------------  30 Mw

Taji 3, NG, Compressor -------------------------------------------------------- 15 Mw

Taji 4, NG, Turbine problem --------------------------------------------------  15 Mw

Taji 5, NG, Pilot Problem ------------------------------------------------------  15 Mw

Taji Mobile, 2, NG, Software problem --------------------------------------  10 Mw

* RED – Denotes out of service since last report

- Generators Scheduled Out of Service as of 2 JAN  04                 1071 Mw

- 2 Thermal units off-line for rehabilitation  ---------------------------------   200 Mw

  - Daura 5 and 6 – 200 Mw – ECD  May 2004

- 6 Thermal units in programmed maintenance --------------------------   623 Mw

  - Dibis 1 – 8 Mw –  ECD Jan 25

  - Baiji  6 -100 Mw –  ECD Jan 19

  - South Baghdad 5   35 Mw – ECD Jan 15

  - Mussaibe 3          200 Mw – ECD TBD (Scheduled Start-up 3 Jan)

  - Nassirya 4           130 Mw – ECD Feb 15

  - Hartha 4              150 Mw – ECD slipped to 23 Jan

- 6 Gas Turbine units off-line for rehabilitation ------------------------------123 Mw

  - Dibis 4, 5,          18 Mw

  - Old Mulla 12      15 Mw

  - Taji 7                 15 Mw

  - Daura 3             20 Mw

  - Khor Zubayr 4   55 Mw

- 5 Gas Turbine units in programmed maintenance------------------------125 Mw

  - Mosil 3                 15 Mw

  - Old Mulla 5,7       30 Mw

  - New Mulla 5        30 Mw

  - Najaf 2                 50 Mw

Transmission:

Countrywide, Iraq’s electrical output continues to be constrained by damaged transmission and distribution lines. The lines have come down due to sabotage and bad weather.  Downed transmission lines increase the probability for complete nationwide blackout by reducing system contingency and causing mechanical damage at power plants. This may cause further temporary blackouts, which have already directly resulted in 1) impacted refineries causing reduced fuel flow to power plants and a subsequent reduction in power supply, and 2) damages in the power plants due to undercurrent causing units to come off-line for unscheduled maintenance.

- Transmission Lines out of service:

400KV

Nassiriya-Khor Zubayr – ECD  May 1

Haditha-Baghdad West – ECD slipped from Jan 24 to Feb 29

Haditha-Qarna – Wasit – ECD slipped from Jan 12 to Jan 31

Baghdad South – Qadisseya – ECD Jan 20

Baiji - Baghdad West #1 – ECD Jan 24

New line - Baghdad East-Baghdad South #2 – ECD Jan 23

Haditha – Qaim – no funding

Baiji – Haditha – no funding/no contractor

Diyala Connection – ECD April 30

132KV

Mosul – Mosul East is sabotaged

Shuwaiba-Toba-Hamar– ECD Dec 30, (delay due to material shortage)

Baghdad West – Jamia – ECD TBD

Omara-Burzegan – Sabotaged. ECD March 2004

Temim- Tuz – ECD TBD

Lines Returned to service:

Muthena GPS – Dour -  Complete Dec 28

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

NG:  NATURAL GAS

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

HYDRO:  WATER POWER