## A-Steam Power Stations
REPORT DATE - 7 January 2004
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 2 |  | 8 | 0 | 8 |  |  | 16 | 24 | #1 prog maint.10 DEC to 25 JAN. #3 FWF.
Baiji | Fuel Oil | 6 | 2 | 100 | 0 | 0 | 95 | 0 | 0 | 195 | 500 | #2 lack of HCL. #3 boiler leak. #6 prog maint. 5 DEC to 19 JAN.
Daura | Fuel Oil | 4 | 1 |  |  | 80 | 0 | 0 | 0 | 80 | 180 | No. 4 Repair of bearing, Nos. 5 & 6: Rehab.
South Baghdad | Fuel Oil | 6 | 2 | 0 | 0 | 20 | 30 | 0 | 0 | 50 | 200 | #1 Boiler Leak, #2 A/H, #6 Thrust bearing, #5 prog maint
Mussaibe | Crude and Fuel Oil | 4 | 2 | 210 | 0 | 0 | 215 |  |  | 425 | 860 | #2 Inspection/Seal treatment, #3 Burner Mgmt. System (BMS)
Nassirya | Crude | 4 | 3 | 130 | 140 | 140 | 0 |  |  | 410 | 600 | #4 prog maint. 28 DEC to 28 JAN.
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 40 | 90 |  | 130 | 160 | #4 only one boiler in operation-degraded
Hartha | Natural Gas and Crude | 4 | 1 | 140 |  |  | 0 |  |  | 140 | 300 | #4 prog maint.
[9 empty] | Total: | 1446 | 2824

## B- Gas_C-Power Stations
Report Date- 7 January 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 130 | 125 | Gas Oil | No. 2 lubricating oil leak | Musil Dam Main | 4 | 3 | 380 | 600
Quds | 2 | 1 | 110 | 160 | Gas Oil | 39 truck #2 C/B problem | Musil Dam reg | 4 | 3 | 36 | 60 | 450
Mosil | 12 | 8 | 125 | 150 | 28 | #1 Rotor Defect. #2 servo ACC. #3 Prog Maint. #9 rotor defect. | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 30 | 30 | 33 | #4 and 5 rehab.. | Haditha Dam | 6 | 2 | 140 | 160 | 300
Old Mulla | 12 | 7 | 90 | 128 | 520 | #1 ACC gear, #2 servo, #5 Prog maint, #7 progm maint, #12 rehab. | Samarra | 3 | 3 | 40 | 55 | 400
New Mulla | 6 | 3 | 95 | 173 | 30 | #4, 5 prog maint, #6 Generator defect | Himrin | 2 | 1 | 22 | 21 | 90
Taji | 7 | 4 | 55 | 55 | 18 | #3 Compressor, #4 Turbine, #7 Rehab. | Hindia | 4 | 3 | 5 | 5
M. Taji | 2 | 1 | 8 | 18 | Natural Gas | #2 software. | Kufa | 4 | 0 | 0 | 0
Daura | 4 | 3 | 70 | 30 | 17 | #3 Rehab |  |  | Total | 733 | 896
Hilla | 4 | 3 | 55 | 64 | 30 | #1 Stopped 1930 cooling system | System Generation |  | 69917 | MWh
Najaf | 3 | 2 | 100 | 129 | 30 | #2 prog maint | Syrian Line Generation |  | 1421 | MWh
Khor | 4 | 3 | 125 | 80 | Natural Gas | #4 Rehab | Turkey Line Generation |  | 1889 | MWh
Shuaiba | 2 | 2 | 4 | 20 | Natural Gas | #1 Stand by | Total Generation |  | 73630 | MWh
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | System Peak Load |  | 3230 | MW
M. Dibis | 4 | 4 | 12 | 24 | Natural Gas |  | Syria Peak Load |  | 54 | MW
Mossil East | 5 | 0 | 0 | 0 | Gas Oil |  | Turkey Peak Load |  | 82 | MW
Hmam/Zafranya | 7 | 0 | 5 |  | Gas Oil |  | Fixed Gen Peak Load |  | 77 | MW
Diesel |  |  | 0 |  | Gas Oil |  | Total Peak Load |  | 3443 | MW
|  | Total | 1024 | 1186 |  |  | Baghdad Load |  | 1236 | MW
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 7 January 2004
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Power transferred from North to Middle 500 MW.
Power transferred from South to Middle 170 MW.
Baghdad | 1236 | 27453 | 1143.875
Duhok | 82 | 1876 | 78.1667
Naynawa | 302 | 6633 | 276.375
Tamim | 121 | 3041 | 126.7083
Salah Aldeen | 180 | 4057 | 169.0417
Anbar | 160 | 3753 | 156.375
Dyala | 70 | 1577 | 65.7083
Babil | 70 | 1801 | 75.0417
Kirbala | 60 | 1394 | 58.0833
Najaf | 90 | 2145 | 89.375
Kadsya | 65 | 1141 | 47.5417
Wasit | 95 | 1775 | 73.9583
Muthana | 56 | 1194 | 49.75
Nasirya | 125 | 2421 | 100.875
Misan | 59 | 1395 | 58.125
Basra | 325 | 6778 | 282.4167