## A-Steam Power Stations
REPORT DATE - 17 January 2004
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 1 |  |  |  | 8 |  |  | 8 | 24 | #1 prog maint; #2 boiler leakeage; #3 prog maint
Baiji | Fuel Oil | 6 | 3 | 90 |  | 95 | 100 |  |  | 285 | 500 | #2 prog. maint; #3 synch at 1340; #5 forced outage; #6 prog maint
Daura | Fuel Oil | 4 | 1 |  |  | 75 |  |  |  | 75 | 180 | #4 rotor repair; #(5+6) Rehab
South Baghdad | Fuel Oil | 6 | 1 |  |  | 20 |  |  |  | 20 | 200 | #1 stopped at 256 boiler leakage; #2 air heater defect; #4 stopped at 1628 boiler leakage; #5 prog maint; #6 stopped at 1115 excit. Fail
Mussaibe | Crude and Fuel Oil | 4 | 3 | 210 | 100 |  | 225 |  |  | 535 | 860 | #1 synch at 1613; #3 stopped at 1454 boiler leakage
Nassirya | Crude | 4 | 3 | 130 | 140 | 150 |  |  |  | 420 | 600 | #4 prog maint. 28 DEC to 28 JAN.
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 30 | 85 |  | 115 | 160 | #4 one boiler in operation
Hartha | Natural Gas and Crude | 4 | 1 | 140 | [5 empty] | 140 | 300 | #1 stopped at 1228 air press. Dropped, synch at 1602; #4 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1598 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date- 17 January 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 130 | 125 | Gas Oil | #1 synch at 1605; #2 lubricating oil leak from bearing | Musil Dam Main | 4 | 3 | 390 | 600
Quds | 2 | 2 | 193 | 160 | Gas Oil | 35 trucks | Musil Dam reg | 4 | 3 | 36 | 60 | 450
Mosil | 12 | 7 | 114 | 150 | 25 | #1 rotor defect; #2 servo + ACC; #3 prog maint; #6 diesel; #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 25 | 30 | 30 | #4 and #5 rehab | Haditha Dam | 6 | 2 | 130 | 160 | 300
Old Mulla | 12 | 8 | 103 | 128 | 450 | #1 ACC gear; #2 servo; #5 prog maint; #12 rehab | Samarra | 3 | 2 | 32 | 55 | 390
New Mulla | 6 | 3 | 94 | 173 | 3 | #4 & #5 prog maint; #6 Generator defect | Himrin | 2 | 1 | 22 | 21 | 90
Taji | 7 | 4 | 62 | 55 | 16 | #3 Compressor; #4 turbine; #7 Rehab | Hindia | 4 | 4 | 5 | 5 | 120
M. Taji | 2 | 1 | 7 | 18 | 16 | #2 software. | Kufa | 4 | 0 | 0 | 0
Daura | 4 | 3 | 59 | 30 | 16 | #3 Rehab |  |  | Total | 725 | 896
Hilla | 4 | 4 | 67 | 64 | 20 | #2 synch at 1725; #3 synch at 836; #4 synch at 1340 | System Generation |  | 74661 | MWh
Najaf | 3 | 2 | 87 | 129 | 19 | #2 prog maint | Syrian Line Generation |  | 1428 | MWh
Khor | 4 | 3 | 50 | 80 | Natural Gas | #4 Rehab | Turkey Line Generation |  | 1944 | MWh
Shuaiba | 2 | 1 | 7 | 20 | Natural Gas | #2 S/B | Total Generation |  | 78033 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas |  | System Peak Load |  | 3442 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 |  |  | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 2 | 12 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 77 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Total Peak Load |  | 3582 | MW
Diesel |  |  | 22 |  | Gas Oil |  | Baghdad Load |  | 1300 | MW
|  | Total | 1045 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
DATE :17/ 1 / 2004
N | GOV. | Average planned load (MW) | Average supplied load (MW) | Deviation
1 | BAGD | 1824 | 1220 | 604
2 | DOHK | 112 | 79 | 33
3 | NYNW | 523 | 290 | 233
4 | TAME | 188 | 123 | 65
5 | SLAH | 243 | 169 | 74
6 | ANBR | 219 | 137 | 82
7 | DYLA | 135 | 62 | 73
8 | BABL | 130 | 72 | 58
9 | KRBL | 99 | 81 | 18
10 | NAJF | 126 | 94 | 32
11 | WAST | 132 | 71 | 61
12 | KADS | 85 | 47 | 38
13 | MUTH | 73 | 46 | 27
14 | THQR | 124 | 108 | 16
15 | MYSN | 75 | 57 | 18
16 | BASR | 310 | 259 | 51
5