Power System Highlights for January 18, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Qudis, Gas Power Generator underwent maintenance yesterday for fuel system cleaning.  The 6-hour downtime resulted in the loss of 120Mw of output. The generator is fully operational at this time.

Generation:

- Daily System peak on 17 Jan – 3487Mw.

- Daily system Demand on 17 Jan – 5,653 Mw (Estimated)

(3487 Actual Generation, + 1860 Load Shed, + 306 Corrected Frequency, = 5653)

- Total generation – 75,891Mwh

- Imported power -  Power from Syria (60Mw) and Turkey (80Mw) included in System Peak

- Generators Returned to Service                                                                           65 MW

South Baghdad 4					20Mw

South Baghdad 6					30 Mw

Taji 4					15Mw

Generators Unscheduled Out of Service as of 17 JAN 04                                           643 Mw

| Dibis 2, SP, Boiler Leak | 8Mw |
| --- | --- |
| Baiji 5, SP, Forced Outage (No ECD) | 100Mw |
| Daura 4, Rotor repair | 100Mw |
| South Baghdad 1, boiler leak | 30Mw |
| South Baghdad 2, Air heater defect | 30Mw |
| Mussaibe 3, SP, Hydraulic test | 150Mw |
| Baiji 2, NG, Lubricating oil leak from bearing | 60Mw |
| Mosil 1, NG, Rotor Defect | 15Mw |
| Mosil 2, NG, Servo problem | 15Mw |
| Mosil 6, NG, diesel | 15Mw |
| Mosil 9, NG, Rotor Defect | 15Mw |
| Old Mulla 1,NG, Acc Gear | 15Mw |
| Old Mulla 2, NG, Servo and Circuit breaker problem | 15Mw |
| * Old Mulla 3, NG, stopped | 15Mw |
| New Mulla 6, NG, Generator Defect | 30Mw |
| Taji 3, NG, Compressor | 15Mw |
| Taji Mobile, 2, NG, Software problem | 10Mw |
| Shuaiba 2, NG, Stand By | 5Mw |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service as of 17 JAN  04                                        1049 Mw

- 2 Thermal units off-line for rehabilitation  ------------------------------------------------   200 Mw

  - Daura 5 and 6      200 Mw – ECD  May 2004

- 6 Thermal units in programmed maintenance -----------------------------------------   531 Mw

  - Dibis 1                      8 Mw – ECD Jan 25

  - Dibis 3                      8 Mw – ECD Feb15

  - Baiji  2                  100 Mw – ECD Mar 04

  - Baiji  6                  100 Mw – ECD Jan 19

  - South Baghdad 5   35 Mw – ECD Jan 15

  - Nassirya 4            130 Mw – ECD Jan 28

  - Hartha 4               150 Mw – ECD slipped to Jan 23

- 6 Gas Turbine units off-line for rehabilitation ---------------------------------------------173 Mw

  - Dibis 4,                    9 Mw -  ECD  Mar 30

  - Dibis 5                     9 Mw – ECD  Jan 29

  - Old Mulla 12          15 Mw

  - Taji 7                     15 Mw

  - Daura 3                  20 Mw

  - Khor Zubayr 4        55 Mw – ECD Jan 31

  - Najaf 2        	       50 Mw - ECD Jan 25

- 5 Gas Turbine units in programmed maintenance--------------------------------------- 145 Mw

  - Mosil 3 	       15 Mw

  - Old Mulla 5             15 Mw

  - New Mulla 4, 5       60 Mw (#5 ECD Mar 31)

  - Khor Zubayr 3        55 Mw

Transmission:

Countrywide, Iraq’s electrical output continues to be constrained by damaged transmission and distribution lines. The lines have come down due to sabotage and bad weather.  Downed transmission lines increase the probability for complete nationwide blackout by reducing system contingency and causing mechanical damage at power plants. This may cause further temporary blackouts, which have already directly resulted in 1) impacted refineries causing reduced fuel flow to power plants and a subsequent reduction in power supply, and 2) damages in the power plants due to undercurrent causing units to come off-line for unscheduled maintenance.

- Transmission Lines out of service:

400KV

Nassiriya-Khor Zubayr – ECD  May 1

Haditha-Baghdad West – ECD slipped from Jan 24 to Mar 15

Hartha-Qarna – Wasit – ECD slipped to Feb 29

Baghdad South – Qadisseya – ECD Jan 20

Baiji - Baghdad West #1 – ECD Feb 10

New line - Baghdad East-Baghdad South #2 – ECD Feb 4

Haditha – Qaim – no funding

Baiji – Haditha – no funding/no contractor

Diyala Connection – ECD April 30

Baiji – Mosul #1 –  ECD Jan 24

132KV

Shuwaiba-Toba-Hamar– ECD Jan 30

Omara-Burzegan – Sabotaged. ECD March 2004

Nejibiya – Hartha  Work Complete on one line, one remaining

Bab- Al Zubair – ECD TBD

Shuwaiba – Bab Al Zubayr 1+2, ECD TBD

SST – Um Qsr ECD TBD

Lines Returned to service:

None reported today

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

NG:  NATURAL GAS

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

HYDRO:  WATER POWER

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil