Power System Highlights for January 25, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

.

Generation:

- Daily System peak on 24 Jan – 4047Mw.

- Daily system Demand on 24 Jan – 5,876 Mw (Estimated)

(4047 Actual Generation, + 1555 Load Shed, + 274 Corrected Frequency, = 5876)

- Total generation – 84,146Mwh

- Imported power -  Power from Syria (60Mw) and Turkey (80Mw) included in System Peak

- Generators Returned to Service   				          0 Mw

None reported

Generators Unscheduled Out of Service as of 24 JAN 04                                           683 Mw

| Dibis 4, SP, Boiler Leak | 8Mw |
| --- | --- |
| *Baiji 4, SP, Boiler Leak | 100Mw |
| Baiji 5, SP, Forced Outage | 100Mw |
| Daura 4, SP, Rotor repair | 100Mw |
| South Baghdad 2, SP, Air heater defect | 30Mw |
| South Baghdad 3, SP, Boiler Leak | 30Mw |
| South Baghdad 6, SP, Boiler Leak | 30Mw |
| Baiji 2, NG, Lubricating oil leak from bearing | 60Mw |
| *Quds 1, NG, stopped | 60Mw |
| Mosil 1, NG, Rotor Defect | 15Mw |
| Mosil 2, NG, Servo problem | 15Mw |
| Mosil 9, NG, Rotor Defect | 15Mw |
| Mosil 11, NG, Earth vault | 15Mw |
| Old Mulla 1,NG, Acc Gear | 15Mw |
| Old Mulla 2, NG, Servo and Circuit breaker problem | 15Mw |
| New Mulla 6, NG, Generator Defect | 30Mw |
| Taji 3, NG, Compressor | 15Mw |
| Taji 4, NG, No Flame | 15Mw |
| Taji Mobile, 2, NG, Software problem | 10Mw |
| Shuaiba 2, NG, Gas Turbine Leak | 5Mw |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service as of 24 JAN  04                                         956 Mw

- 2 Thermal units off-line for rehabilitation  ------------------------------------------------   200 Mw

  - Daura 5 and 6      200 Mw – ECD  May 2004

- 6 Thermal units in programmed maintenance -----------------------------------------   523 Mw

  - Dibis 3                      8 Mw – ECD Feb15

  - Baiji  2                  100 Mw – ECD Mar 04

  - Baiji  6                  100 Mw – ECD Slipped Feb 3

  - South Baghdad 5   35 Mw – ECD Slipped TBD

  - Nassirya 4            130 Mw – ECD Jan 28

  - Hartha 4               150 Mw – ECD slipped to Jan 30

- 6 Gas Turbine units off-line for rehabilitation ---------------------------------------------173 Mw

  - Dibis 4,                     9 Mw -  ECD  Mar 30

  - Dibis 5                      9 Mw – ECD  Jan 29

  - Old Mulla 12    	    15 Mw

  - Taji 7    		    15 Mw

  - Daura 3 		    20 Mw

  - Khor Zubayr 4 	    55 Mw – ECD Jan 31

  - Najaf 2 		    50 Mw -  ECD Jan 25

- 5 Gas Turbine units in programmed maintenance---------------------------------------  60 Mw

  - Old Mulla 5             15 Mw

  - Old Mulla 10           15 Mw -  ECD Feb 05

  - New Mulla 4           30 Mw – ECD Mar 31

Transmission:

Countrywide, Iraq’s electrical output continues to be constrained by damaged transmission and distribution lines. The lines have come down due to sabotage and bad weather.  Downed transmission lines increase the probability for complete nationwide blackout by reducing system contingency and causing mechanical damage at power plants. This may cause further temporary blackouts, which have already directly resulted in 1) impacted refineries causing reduced fuel flow to power plants and a subsequent reduction in power supply, and 2) damages in the power plants due to undercurrent causing units to come off-line for unscheduled maintenance.

- Transmission Lines out of service:

400KV

Nassiriya-Khor Zubayr – ECD  May 1

Haditha-Baghdad West – ECD slipped from Jan 24 to Mar 15

Hartha-Qarna – Wasit – ECD slipped to Feb 29

Baghdad South – Qadisseya – ECD Jan 20

Baiji - Baghdad West #1 – ECD Feb 10

New line - Baghdad East-Baghdad South #2 – ECD Feb 4

Haditha – Qaim – no funding

Baiji – Haditha – no funding/no contractor

Diyala Connection – ECD April 30

Baiji – Mosul #1 –  ECD Jan 24

132KV

Shuwaiba-Toba-Hamar– ECD Jan 30

Omara-Burzegan – Sabotaged. ECD March 2004

Nejibiya – Hartha  Work Complete on one line, one remaining

Bab- Al Zubair – ECD TBD

Shuwaiba – Bab Al Zubayr 1+2, ECD TBD

SST – Um Qsr ECD TBD

Lines Returned to service:

None reported today

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

NG:  NATURAL GAS

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

HYDRO:  WATER POWER

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil