## A-Steam Power Stations
REPORT DATE - 25 January 2004
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 2 | 8 | 8 |  |  |  |  | 16 | 24 | #3 prog maint; #4 Boiler Leakage
Baiji | Fuel Oil | 6 | 2 | 90 |  | 85 |  |  |  | 175 | 500 | #2 Prog. maint. #4 stopped at 0357 Boiler leakage #5 forced outage. #6 prog maint
Daura | Fuel Oil | 4 | 1 |  |  | 75 |  |  |  | 75 | 180 | #4 rotor repair; #(5+6) Rehab
South Baghdad | Fuel Oil | 6 | 2 | 25 |  |  | 25 |  |  | 50 | 200 | #2 air heater defect; #3 stopped at 1625 boiler leakage; #5 prog maint; #6 boiler leakage
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 | 80 | 150 | 210 |  |  | 640 | 860 | #2 limited to C.W. prepairing; #3 boiler check
Nassirya | Crude | 4 | 3 | 130 | 150 | 170 |  |  |  | 450 | 600 | #4 prog maint. 28 DEC to 28 JAN.
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 80 | 85 |  | 165 | 160
Hartha | Natural Gas and Crude | 4 | 1 | 90 | [5 empty] | 90 | 300 | #1FDF; #4 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1661 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date- 25 January 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 135 | 125 | Gas Oil | #2 lubricating oil leak from bearing | Musil Dam Main | 4 | 3 | 420 | 600
Quds | 2 | 1 | 112 | 160 | Gas Oil | 41trucks; #2 C/B problem | Musil Dam reg | 4 | 4 | 44 | 60 | 750
Mosil | 12 | 8 | 126 | 150 | 23 | #1 rotor defect; #2 servo + ACC; #9 rotor defect; #11 stopped at 0021 11kv earth fault | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 30 | 30 | 30 | #4 and #5 rehab | Haditha Dam | 6 | 2 | 140 | 160 | 250
Old Mulla | 12 | 7 | 96 | 128 | 460 | #1 ACC gear, #2 servo, #5 prog maint, #10 prog maint; #12 rehab | Samarra | 3 | 2 | 34 | 55 | 340
New Mulla | 6 | 3 | 107 | 173 | 320 | #4 prog maint; #6 Generator defect | Himrin | 2 | 1 | 23 | 21 | 330
Taji | 7 | 4 | 68 | 55 | 19 | #3 Compressor; #4 flame def; #7 Rehab. | Hindia | 4 | 4 | 5 | 5
M. Taji | 2 | 1 | 7 | 18 |  | #2 software. | Kufa | 4 | 0 | 0 | 0
Daura | 4 | 3 | 75 | 30 | 17 | #3 Rehab |  |  | Total | 776 | 896
Hilla | 4 | 4 | 70 | 64 | 22 | #1 synch at 1720 | System Generation |  | 80710 | MWh
Najaf | 3 | 2 | 19 | 129 | 80 | #2 prog maint | Syrian Line Generation |  | 1433 | MWh
Khor | 4 | 3 | 125 | 80 | Natural Gas | #3 synch at 1510; #4 Rehab | Turkey Line Generation |  | 2021 | MWh
Shuaiba | 2 | 1 | 6 | 20 | Natural Gas | #2 gas turbine check | Total Generation |  | 84146 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3780 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 12 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 2 | 18 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 127 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 4047 | MW
Diesel |  |  | 24 |  | Gas Oil |  | Baghdad Load |  | 1494 | MW
|  | Total | 1042 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 25 January 2004
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Power transferred from North to Middle 700 MW.
Power transferred from South to Middle 150 MW.
Baghdad | 1494 | 30689 | 1279
Duhok | 80 | 1920 | 80
Naynawa | 400 | 9114 | 380
Tamim | 138 | 3500 | 146
Salah Aldeen | 199 | 4668 | 195
Anbar | 185 | 3904 | 163
Dyala | 113 | 2109 | 88
Babil | 95 | 2371 | 99
Kirbala | 90 | 2088 | 87
Najaf | 100 | 2615 | 109
Kadsya | 60 | 1368 | 57
Wasit | 85 | 1999 | 83
Muthana | 52 | 1277 | 53
Nasirya | 122 | 2670 | 111
Misan | 60 | 1395 | 58
Basra | 340 | 6929 | 289