## A-Steam Power Stations
REPORT DATE - 26 January 2004
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 2 | 8 | 8 |  |  |  |  | 16 | 24 | #3 prog maint; #4 stopped at 2102 boiler leakage
Baiji | Fuel Oil | 6 | 2 | 90 |  | 95 |  |  |  | 185 | 500 | #2 prog. maint; #4 starting; #5 forced outage; #6 prog maint
Daura | Fuel Oil | 4 | 1 |  |  | 75 |  |  |  | 75 | 180 | #4 rotor repair; #(5+6) Rehab
South Baghdad | Fuel Oil | 6 | 1 |  |  | 30 |  |  |  | 30 | 200 | #1 stopped at 1105 boiler leakage; #2 air heater defect; #3 synch at 1720; #4 stopped at 2250 vacuum pump; #5 prog maint; #6 boiler leakage
Mussaibe | Crude and Fuel Oil | 4 | 4 | 200 | 85 | 150 | 210 |  |  | 645 | 860 | #2 limited to C.W.P.; #3 boiler check
Nassirya | Crude | 4 | 3 | 130 | 150 | 150 |  |  |  | 430 | 600 | #4 prog maint. 28 DEC to 28 JAN.
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 80 | 85 |  | 165 | 160
Hartha | Natural Gas and Crude | 4 | 1 | 90 | [5 empty] | 90 | 300 | #1 limited to FDF; #4 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1636 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date- 26 January 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 125 | 125 | Gas Oil | #2 lubricating oil leak from bearing | Musil Dam Main | 4 | 3 | 420 | 600
Quds | 2 | 2 | 135 | 160 | Gas Oil | 37 trucks, #1 synch at 2010 | Musil Dam reg | 4 | 4 | 45 | 60 | 750
Mosil | 12 | 7 | 11 | 150 | 29 | #1 rotor defect; #2 servo + ACC; #3 stopped at 2301 bleed valve; #6 stopped at 956 diesel; #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 27 | 30 | 32 | #4 and #5 rehab | Haditha Dam | 6 | 2 | 140 | 160 | 250
Old Mulla | 12 | 7 | 97 | 128 | 480 | #1 ACC gear, #2 servo, #5 prog maint, #10 prog maint; #12 rehab | Samarra | 3 | 2 | 32 | 55 | 340
New Mulla | 6 | 3 | 103 | 173 | 32 | #1 & #4 prog maint; #5 synch at 1350; #6 Generator defect | Himrin | 2 | 1 | 22 | 21 | 90
Taji | 7 | 4 | 61 | 55 | 20 | #3 Compressor; #4 flame def; #7 rehab | Hindia | 4 | 4 | 5 | 5 | 130
M. Taji | 2 | 1 | 7 | 18 | 20 | #2 software. | Kufa | 4 | 1 | 1 | 0 | 33
Daura | 4 | 3 | 75 | 30 | 18 | #3 Rehab |  |  | Total | 775 | 896
Hilla | 4 | 4 | 68 | 64 | 22 |  | System Generation |  | 80350 | MWh
Najaf | 3 | 2 | 91 | 129 | 20 | #2 prog maint | Syrian Line Generation |  | 1423 | MWh
Khor | 4 | 3 | 120 | 80 | Natural Gas | #4 rehab | Turkey Line Generation |  | 1975 | MWh
Shuaiba | 2 | 1 | 6 | 20 | Natural Gas | #2 S/B | Total Generation |  | 83750 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3469 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 2 | 12 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 127 | MW
Hmam/Zafranya | 7 | 1 | 1 |  | Gas Oil |  | Total Peak Load |  | 3736 | MW
Diesel |  |  | 25 |  | Gas Oil |  | Baghdad Load |  | 1460 | MW
|  | Total | 983 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 26 January, 2004
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Power transferred from North to Middle 670 MW.
Power transferred from South to Middle 175 MW.
Baghdad | 1460 | 30291 | 1262
Duhok | 80 | 1905 | 79
Naynawa | 300 | 7700 | 321
Tamim | 121 | 3172 | 132
Salah Aldeen | 190 | 4608 | 192
Anbar | 180 | 4011 | 167
Dyala | 75 | 1937 | 81
Babil | 85 | 2263 | 94
Kirbala | 80 | 1960 | 82
Najaf | 90 | 2455 | 102
Kadsya | 60 | 1373 | 57
Wasit | 80 | 1950 | 81
Muthana | 45 | 1262 | 53
Nasirya | 120 | 2784 | 116
Misan | 50 | 1488 | 62
Basra | 300 | 7193 | 300