Power System Highlights for January 28, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Nassirya 4 returned programmed maintenance and is operational.

Generation:

- Daily System peak on 27 Jan – 4104Mw.

- Daily system Demand on 27 Jan – 5,922 Mw (Estimated)

(4104 Actual Generation, + 1500 Load Shed, + 318 Corrected Frequency, = 5922)

- Total generation – 87,494Mwh

- Imported power -  Power from Syria (60Mw) and Turkey (82Mw) included in System Peak

- Generators Returned to Service   				          335 Mw

Baiji 4				          100 Mw

South Baghdad 1       					30 Mw

Nassirya 4				          130 Mw

South Baghdad 6			                        30 Mw

Mosil 2					15 Mw

Mosil 6				            15 Mw

Taji 4				            15 Mw

Generators Unscheduled Out of Service as of 27 JAN 04                                           579 Mw

| *Dibis 1, SP, Turbine Vibration | 8Mw |
| --- | --- |
| Dibis 4, SP, Boiler Leak | 8Mw |
| Baiji 5, SP, Forced Outage | 100Mw |
| Daura 4, SP, Rotor repair | 100Mw |
| South Baghdad 4, SP, Boiler Leak | 30Mw |
| South Baghdad 2, SP, Air heater defect | 30Mw |
| *Najebia 6, SP, Natural Gas system trouble | 100Mw |
| Baiji 2, NG, Lubricating oil leak from bearing | 60Mw |
| Mosil 1, NG, Rotor Defect | 15Mw |
| Mosil 3, NG, Bleed Valve | 15Mw |
| Mosil 9, NG, Rotor Defect | 15Mw |
| Old Mulla 1,NG, Acc Gear | 15Mw |
| Old Mulla 2, NG, Servo and Circuit breaker problem | 15Mw |
| New Mulla 6, NG, Generator Defect | 30Mw |
| Taji 3, NG, Compressor | 15Mw |
| Taji Mobile, 2, NG, Software problem | 15Mw |
| Shuaiba 2, NG, Stand by | 8Mw |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service as of 27 JAN  04                                         801 Mw

- 2 Thermal units off-line for rehabilitation  ------------------------------------------------   200 Mw

  - Daura 5 and 6      200 Mw – ECD  May 2004

- 6 Thermal units in programmed maintenance -----------------------------------------   393 Mw

  - Dibis 3                      8 Mw – ECD Feb15

  - Baiji  2                  100 Mw – ECD Mar 04

  - Baiji  6                  100 Mw – ECD Feb 3

  - South Baghdad 5   35 Mw – ECD Slipped TBD

  - Hartha 4               150 Mw – ECD Jan 30

- 6 Gas Turbine units off-line for rehabilitation ---------------------------------------------118 Mw

  - Dibis 4,                     9 Mw -  ECD  Mar 30

  - Dibis 5                      9 Mw – ECD  Jan 29

  - Old Mulla 12    	    15 Mw

  - Taji 7    		    15 Mw

  - Daura 3 		    20 Mw

  - Najaf 2 		    50 Mw -  ECD Jan 25

- 5 Gas Turbine units in programmed maintenance---------------------------------------  90 Mw

  - Old Mulla 5             15 Mw

  - Old Mulla 10           15 Mw -  ECD Feb 05

  - New Mulla 4           30 Mw – ECD Mar 31

  - New Mulla 1           30 Mw – ECD Feb 29

Transmission:

Countrywide, Iraq’s electrical output continues to be constrained by damaged transmission and distribution lines. The lines have come down due to sabotage and bad weather.  Downed transmission lines increase the probability for complete nationwide blackout by reducing system contingency and causing mechanical damage at power plants. This may cause further temporary blackouts, which have already directly resulted in 1) impacted refineries causing reduced fuel flow to power plants and a subsequent reduction in power supply, and 2) damages in the power plants due to undercurrent causing units to come off-line for unscheduled maintenance.

- Transmission Lines out of service:

400KV

Nassiriya-Khor Zubayr – ECD  May 1

Haditha-Baghdad West – ECD slipped from Jan 24 to Mar 15

Hartha-Qarna – Wasit – ECD slipped to Feb 29

Baiji - Baghdad West #1 – ECD Feb 10

New line - Baghdad East-Baghdad South #2 – ECD Feb 4

Haditha – Qaim – no funding

Baiji – Haditha – no funding/no contractor

Diyala Connection – ECD April 30

132KV

Shuwaiba-Toba-Hamar– ECD Jan 30

Omara-Burzegan – Sabotaged. ECD March 2004

Nejibiya – Hartha  Work Complete on one line, one remaining

Bab- Al Zubair – ECD TBD

Shuwaiba – Bab Al Zubayr 1+2, ECD TBD

SST – Um Qsr ECD TBD

Lines Returned to service:

None

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

NG:  NATURAL GAS

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

HYDRO:  WATER POWER

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil