## A-Steam Power Stations
REPORT DATE - 28 January 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 |  | 8 |  |  |  |  | 8 | 24 | #1 turbine vib; #3 prog maint; #4 boiler leakage
Baiji | Fuel Oil | 6 | 3 | 85 |  | 85 | 95 |  |  | 265 | 500 | #2 prog maint; #5 forced outage; #6 testing
Daura | Fuel Oil | 4 | 1 |  |  | 75 |  |  |  | 75 | 180 | #4 rotor repair; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 3 | 30 |  | 25 |  |  | 30 | 85 | 200 | #1synch at 2255; #2 air heater defect; #4 stopped at 2023 DLL; #5 prog maint; #6 synch at 1415
Mussaibe | Crude and Fuel Oil | 4 | 4 | 200 | 175 | 150 | 220 |  |  | 745 | 860 | #1limited F.W.P; #3 boiler check
Nassirya | Crude | 4 | 4 | 130 | 150 | 160 | 65 |  |  | 505 | 600 | #4 synch at 1745
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 35 |  |  | 35 | 160 | #4 one boiler in operation; #5 stopped at 419 NG sys trouble
Hartha | Natural Gas and Crude | 4 | 1 | 75 | [5 empty] | 75 | 300 | #1 FDF; #4 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1793 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date - 28 January 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 125 | 125 | Gas Oil | #2 lub oil leak from bearing | Musil Dam Main | 4 | 4 | 570 | 600 | #3 synch at 1300
Quds | 2 | 2 | 175 | 160 | Gas Oil | 42 trucks | Musil Dam reg | 4 | 4 | 46 | 60 | 750
Mosil | 12 | 9 | 136 | 150 | 28 | #1 rotor defec; #2 synch at 305; #3 bleed valve; #6 synch at 1435; #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 29 | 30 | 31 | #4 & #5 rehab | Haditha Dam | 6 | 2 | 120 | 160 | 250
Old Mulla | 12 | 7 | 95 | 128 | 540 | #1 ACC great; #2 servo; #5 prog maint; #10 prog main; #12 needs rehab | Samarra | 3 | 2 | 33 | 55 | 350
New Mulla | 6 | 3 | 105 | 173 | 3.5 | #1 & #4 prog maint; #6 generator defect | Himrin | 2 | 1 | 23 | 21 | 130
Taji | 7 | 5 | 61 | 55 | 18 | #3 compressor; #4 synch at 1600; #7 needs rehab | Hindia | 4 | 4 | 5 | 5 | 140
M. Taji | 2 | 1 | 8 | 18 | 18 | #2 software | Kufa | 4 |  |  | 0
Daura | 4 | 3 | 72 | 30 | 17 | #3 needs rehab |  |  | Total | 907 | 896
Hilla | 4 | 4 | 70 | 64 | 20 |  | System Generation |  | 84006 | MWh
Najaf | 3 | 2 | 85 | 129 | 19 | #2 prog maint | Syrian Line Generation |  | 1460 | MWh
Khor | 4 | 3 | 120 | 80 | Natural Gas | #4 rehab | Turkey Line Generation |  | 2028 | MWh
Shuaiba | 2 | 1 | 8 | 20 | Natural Gas | #2 S/B | Total Generation |  | 87494 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3835 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 12 | 24 | Natural Gas |  | Turkey Peak Load |  | 82 | MW
Mossil East | 5 | 2 | 12 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 127 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Total Peak Load |  | 4104 | MW
Diesel |  |  | 37 |  | Gas Oil |  | Baghdad Load |  | 1550 | MW
|  | Total | 1163 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 28 January 2004
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Power transferred from North to Middle 770 MW.
Power transferred from South to Middle 200 MW.
Baghdad | 1550 | 31164 | 1299
Duhok | 82 | 1894 | 79
Naynawa | 350 | 8304 | 346
Tamim | 165 | 3511 | 146
Salah Aldeen | 195 | 4801 | 200
Anbar | 180 | 4304 | 179
Dyala | 100 | 2424 | 101
Babil | 110 | 2323 | 97
Kirbala | 95 | 1963 | 82
Najaf | 105 | 2361 | 98
Kadsya | 60 | 1576 | 66
Wasit | 95 | 2071 | 86
Muthana | 65 | 1425 | 59
Nasirya | 130 | 2849 | 119
Misan | 85 | 1418 | 59
Basra | 325 | 7400 | 308