Daily Power System Highlights for January 29, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:  Hilla, 1,2,3,4 and Najaf 1,3 were all out of service due to natural gas pipeline leak.  This leak resulted in a 170 mw loss.

Generation:

Peak Power 4112Mw, 87,486 Mw hours, 7-day Avg. 3977 Mw

Generators Returned to Service	108 Mw

Dibis 4	8 Mw

Najebia 5	100 Mw

Generators Unscheduled Out of Service                                                                        798 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 1 | SP | Turbine vibration | 8 |
| Baiji 5, | SP | Forced Outage (No ECD) | 30 |
| Daura 4 | SP | Rotor repair | 25 |
| South Baghdad 2 | SP | Air HeaterLeak | 30 |
| South Baghdad 4 | SP | Boiler Leak | 30 |
| * Nassirya 3 | SP | Boiler Leak | 160 |
| Baiji 2, | CP | Lubricating oil leak | 40 |
| * Qudis | CP | Fuel Pressure | 90 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 3 | CP | Bleeder valve | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo and Circuit breaker | 15 |
| New Mulla 6 | CP | Generator Defect | 15 |
| Taji 3, | CP | Compressor | 15 |
| * Taji 5, | CP | Stopped, Unknown Reason | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |
| * Hilla, 1,2,3,4 | CP | Natural gas Pipeline Leak | 70 |
| * Najaf 1,3 | CP | Natural Gas Pipeline Leak | 100 |
| Shuaiba 2, | CP | Gas Turbine Leak | 80 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service 	    854 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 01Mar | 100 |
| Baiji 6 | SP | M | Bechtel | 5 Dec 03 | 03Feb | 100 |
| Daura 3 | CP | R | RIE/ME | 1 Mar 03 | TBD | 20 |
| Daura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Daura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME/GRD | 30Dec 03 | 15 Feb | 8 |
| Dibis 4 | CP | R | ME/Bechtel | Sep 03 | 30 Mar | 18 |
| Dibis 5 | CP | R | ME/Bechtel | Sep 03 | 6 Feb | 18 |
| Hartha 4 | SP | M | ME/Bechtel | 23Oct 03 | 1 Feb | 150 |
| Khor Zubayr 4 | CP | R | RIE/GRD | 20Dec03 | 31 Jan | 55 |
| Najaf 2 | CP | R | RIE/GRD | 5 Dec 03 | 30 Apr | 50 |
| New Mulla 1 | CP | M | RIE/GRD | 13 Jan 04 | 15 Feb | 30 |
| New Mulla 4 | CP | M | RIE/GRD | 3 Jan 04 | 31 Mar | 30 |
| Old Mulla 5 | CP | M | RIE/GRD | 1 Nov 03 | 15 Feb | 15 |
| Old Mulla 10 | CP | M | RIE/GRD | 6 Jan 04 | 5 Feb | 15 |
| Old Mulla 12 | CP | R | RIE/GRD | 1 Oct 03 | TBD | 15 |
| South Baghdad 5 | SP | M | ME/Bechtel | 1 Mar 03 | 6 Feb | 35 |
| Taji 7 | CP | R | RIE/GRD | 1 Oct 03 | TBD | 15 |

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 1 May |  |
| Haditha-Baghd West | 400 | Sabotage | GRD |  | 15 Mar | 8 towers complete/236 req’d |
| Hartha-Qarna – Wasit | 400 | Sabotage | GRD |  | 29 Feb | 178 towers complete/293 req’d |
| Baghd South – Diwaniya | 400 | Sabotage | GRD |  | Complete | 27 towers complete/27 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD |  | 10 Feb | 38 towers complete/58 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD |  | 31 Jan | 79 towers complete/81 req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No Contractor |
| Baiji – Haditha | 400 | Sabotage | ME |  | TBD | No contractor |
| Diyala Connection | 400 | Sabotage | ME |  | 30 Apr |  |
| Baiji – Mosul | 400 | Sabotage | ME |  | Complete |  |
| Mosul – Mosul East | 132 | Sabotage | GRD |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | TBD |  |
| Baghd West – Jamia | 132 | Sabotage | GRD |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 Mar |  |
| Temim- Tuz | 132 | Sabotage | GRD |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | GRD |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| Report Date - 29 January 2004 |
| --- |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Power transferred from North to Middle 810 MW. |
| Power transferred from South to Middle 190 MW. |
| Baghdad | 1530 | 31834 | 1326 |
| Duhok | 80 | 1934 | 81 |
| Naynawa | 330 | 8657 | 361 |
| Tamim | 175 | 3624 | 151 |
| Salah Aldeen | 195 | 5043 | 210 |
| Anbar | 180 | 4391 | 183 |
| Dyala | 120 | 2446 | 102 |
| Babil | 100 | 2476 | 103 |
| Kirbala | 97 | 1929 | 80 |
| Najaf | 115 | 2473 | 103 |
| Kadsya | 56 | 1425 | 59 |
| Wasit | 98 | 2125 | 89 |
| Muthana | 58 | 1380 | 58 |
| Nasirya | 130 | 2866 | 119 |
| Misan | 59 | 1170 | 49 |
| Basra | 250 | 6295 | 262 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

LEGEND OF MAINTENANCE ORGANIZATIONS

ME:  Ministry of Electricity

RIE: Restore Iraq Electricity, Formerly TF RIE

GRD: Gulf Region Division

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil