## A-Steam Power Stations
REPORT DATE - 29 January 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 |  | 8 |  | 8 |  |  | 16 | 24 | #1 turbine vib; #3 prog maint; #4 synch at 830
Baiji | Fuel Oil | 6 | 3 | 80 |  | 95 | 95 |  |  | 270 | 500 | #2 prog maint; #5 forced outage; #6 testing
Daura | Fuel Oil | 4 | 1 |  |  | 75 |  |  |  | 75 | 180 | #4 rotor repair; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 3 | 35 |  | 25 |  |  | 30 | 90 | 200 | #2 air heater defect; #4 DLL; #5 prog maint
Mussaibe | Crude and Fuel Oil | 4 | 4 | 180 | 95 | 165 | 225 |  |  | 665 | 860 | #1 limited FWP; #3 boiler check
Nassirya | Crude | 4 | 3 | 130 | 155 |  | 90 |  |  | 375 | 600 | #3 stopped at 2302 boiler leakage
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 88 |  |  | 88 | 160 | #5 synch at 1822
Hartha | Natural Gas and Crude | 4 | 1 | 80 | [5 empty] | 80 | 300 | #1 FDF; #4 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1659 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date - 29 January 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 120 | 125 | Gas Oil | #2 lub oil leak from bearing | Musil Dam Main | 4 | 4 | 580 | 600
Quds | 2 | 1 | 110 | 160 | Gas Oil | #2 stopped at 1645 fuel press low; 40 trucks | Musil Dam reg | 4 | 3 | 30 | 60 | 1000
Mosil | 12 | 9 | 139 | 150 | 24 | #1 rotor defect; #3 bleed valve; #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 28 | 30 | 30 | #4 & #5 rehab | Haditha Dam | 6 | 2 | 120 | 160 | 250
Old Mulla | 12 | 7 | 103 | 128 | 480 | #1 ACC gear; #2 servo; #5 prog maint; #10 prog maint; #12 needs rehab | Samarra | 3 | 2 | 33 | 55 | 350
New Mulla | 6 | 3 | 109 | 173 | 3.1 | #1 & #4 prog maint; #6 generator defect | Himrin | 2 | 1 | 22 | 21 | 130
Taji | 7 | 4 | 64 | 55 | 17 | #3 compressor; #5 stopped at 1820; #7 needs rehab | Hindia | 4 | 4 | 5 | 5 | 140
M. Taji | 2 | 1 | 8 | 18 | 17 | #2 software | Kufa | 4 |  |  | 0
Daura | 4 | 3 | 70 | 30 | 16 | #3 needs rehab |  |  | Total | 900 | 896
Hilla | 4 |  |  | 64 | 9 | NGPL at 1831 | System Generation |  | 84040 | MWh
Najaf | 3 |  |  | 129 |  | #2 prog maint NGPL at 1831; #3 stopped at 1930 shortage of gas oil | Syrian Line Generation |  | 1441 | MWh
Khor | 4 | 3 | 120 | 80 | Natural Gas | #4 rehab | Turkey Line Generation |  | 2005 | MWh
Shuaiba | 2 | 1 | 5 | 20 | Natural Gas | #2 S/B | Total Generation |  | 87486 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3726 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 2 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 246 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Total Peak Load |  | 4112 | MW
Diesel |  |  | 42 |  | Gas Oil |  | Baghdad Load |  | 1530 | MW
|  | Total | 955 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 29 January 2004
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Power transferred from North to Middle 810 MW
Power transferred from South to Middle 190 MW
Baghdad | 1530 | 31834 | 1326
Duhok | 80 | 1934 | 81
Naynawa | 330 | 8657 | 361
Tamim | 175 | 3624 | 151
Salah Aldeen | 195 | 5043 | 210
Anbar | 180 | 4391 | 183
Dyala | 120 | 2446 | 102
Babil | 100 | 2476 | 103
Kirbala | 97 | 1929 | 80
Najaf | 115 | 2473 | 103
Kadsya | 56 | 1425 | 59
Wasit | 98 | 2125 | 89
Muthana | 58 | 1380 | 58
Nasirya | 130 | 2866 | 119
Misan | 59 | 1170 | 49
Basra | 250 | 6295 | 262