Daily Power System Highlights for February 1, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Generation:

Peak Power 4214Mw, 93513 Mw hours, 7-day Avg. 4091 Mw

Generators Returned to Service                                                                                             8 Mw

Dibis 1						8 Mw

Generators Unscheduled Out of Service	763 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| *Dibis 4 | SP | NG system trouble | 8 |
| Baiji 4 | SP | Boiler Leak | 100 |
| Baiji 5, | SP | Forced Outage (No ECD) | 30 |
| Daura 4 | SP | Rotor repair | 25 |
| *South Baghdad 1 | SP | Air Heater | 30 |
| South Baghdad 2 | SP | Boiler Leak | 30 |
| South Baghdad 4 | SP | Boiler Leak | 30 |
| Nassirya 3 | SP | Boiler Leak | 150 |
| *Najebia | SP | Steam Leak | 90 |
| Baiji 2, | CP | Lubricating oil leak | 40 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 3 | CP | Bleeder valve | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo and Circuit breaker | 15 |
| New Mulla 6 | CP | Generator Defect | 15 |
| Taji 3, | CP | Compressor | 15 |
| *Taji 4 | CP | Combustion chamber temp. | 15 |
| Taji 5, | CP | Turbine vibration | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |
| Shuaiba 2, | CP | Gas Turbine Leak | 80 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service 	874 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 01Mar | 100 |
| Baiji 6 | SP | M | Bechtel | 5 Dec 03 | 03Feb | 100 |
| Daura 3 | CP | R | RIE/ME | 1 Mar 03 | TBD | 20 |
| Daura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Daura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME/Bechtel | 30Dec 03 | 15 Feb | 8 |
| Dibis 4 | CP | R | ME/GRD | Sep 03 | 30 Mar | 18 |
| Dibis 5 | CP | R | ME/Bechtel | Sep 03 | 6 Feb | 18 |
| Hartha 4 | SP | M | ME/Bechtel | 23Oct 03 | 1 Feb | 150 |
| Khor Zubayr 4 | CP | R | RIE/GRD | 20Dec03 | 31 Jan | 55 |
| Najaf 2 | CP | R | RIE/GRD | 5 Dec 03 | 30 Apr | 50 |
| New Mulla 1 | CP | M | RIE/GRD | 13 Jan 04 | 15 Feb | 30 |
| New Mulla 4 | CP | M | RIE/GRD | 3 Jan 04 | 31 Mar | 30 |
| Old Mulla 5 | CP | M | RIE/GRD | 1 Nov 03 | 15 Feb | 15 |
| Old Mulla 10 | CP | M | RIE/GRD | 6 Jan 04 | 5 Feb | 15 |
| Old Mulla 12 | CP | R | RIE/GRD | 1 Oct 03 | TBD | 15 |
| South Baghdad 5 | SP | M | ME/Bechtel | 1 Mar 03 | 6 Feb | 35 |
| Taji 7 | CP | R | RIE/GRD | 1 Oct 03 | TBD | 15 |

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 1 May |  |
| Haditha-Baghd West | 400 | Sabotage | RIE/GRD |  | 15 Mar | 28 towers complete/236 req’d |
| Hartha-Qarna – Wasit | 400 | Sabotage | RIE/GRD |  | 29 Feb | 208 towers complete/293 req’d |
| Baghd South – Diwaniya | 400 | Sabotage | RIE/GRD |  | Complete | 27 towers complete/27 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | RIE/GRD |  | 10 Feb | 60 towers complete/66 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | RIE/GRD |  | 10 Feb | 81 towers complete/81 req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No Contract awarded |
| Baiji – Haditha | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Diyala Connection | 400 | Sabotage | ME |  | 30 Apr |  |
| Baiji – Mosul | 400 | Damaged | ME |  | Complete |  |
| Mosul – Mosul East | 132 | Sabotage | RIE/GRD |  | TBD |  |
| Dibis/Irbil-Azadi/Quarqush | 132 | New Line | RIE/GRD |  |  |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | TBD |  |
| Baghd West – Jamia | 132 | Sabotage | RIE/GRD |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 Mar |  |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| Report Date - 1 February 2004 |  |  |
| --- | --- | --- |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Power transferred from North to Middle 780 MW. |
| Power transferred from South to Middle 100MW. |  |
| Baghdad | 1450 |  |  |
| Duhok | 80 |  |  |
| Naynawa | 360 |  |  |
| Tamim | 150 |  |  |
| Salah Aldeen | 227 |  |  |
| Anbar | 185 |  |  |
| Dyala | 75 |  |  |
| Babil | 109 |  |  |
| Kirbala | 111 |  |  |
| Najaf | 105 |  |  |
| Kadsya | 65 |  |  |
| Wasit | 85 |  |  |
| Muthana | 60 |  |  |
| Nasirya | 110 |  |  |
| Misan | 70 |  |  |
| Basra | 310 |  |  |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil