Daily Power System Highlights for February 11, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:  All-time high for Megawatt hours produced, 93,916

Generation:

Peak Power 4230Mw, 93,916Mw hours, 7-day Avg. 3992Mw

Generators Returned to Service                                                                                    130 Mw

Baiji 6, SP	100 Mw

South Baghdad 5                                                                                                              30 Mw

Generators Unscheduled Out of Service					  738 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 2 | SP | Boiler leak | 8 |
| Baiji 1 | SP | Boiler Leak | 90 |
| Daura 3 | SP | Boiler Leak | 65 |
| Daura 4 | SP | Rotor repair | 65 |
| South Baghdad 1 | SP | Boiler Leakage | 30 |
| South Baghdad 2 | SP | Air Heater | 30 |
| South Baghdad 6 | SP | Boiler Leak | 30 |
| Baiji 2, | CP | Lubricating oil leak | 110 |
| Hilla 2 | CP | Servo | 15 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 3 | CP | Bleeder Valve | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo and Circuit breaker | 15 |
| New Mulla 6 | CP | Generator Defect | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |
| * Hilla, 1,2,3,4 | CP | Stopped to install trans line | 80 |
| Shuaiba 2, | CP | Stand By | 80 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service 	1001 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 4 Mar | 100 |
| Baiji 6 | SP | M | Bechtel | 5 Dec 03 | 18 Feb | 100 |
| Daura 3 | CP | R | GRD/RIE | 1 Mar 03 | 1 Jun | 20 |
| Daura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Daura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME | 30Dec 03 | 15 Feb | 8 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 30 Mar | 18 |
| Hartha 4 | SP | M | ME/Bechtel | 23Oct 03 | 14 Feb | 150 |
| Khor Zubayr 4 | CP | R | GRD/RIE | 20Dec03 | 14 Feb | 55 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 7 Mar | 180 |
| Najaf 2 | CP | M | GRD/RIE | 5 Dec 03 | 30 Apr | 50 |
| New Mulla 1 | CP | M | GRD/RIE | 13 Jan 04 | 1 Jun | 30 |
| New Mulla 4 | CP | M | GRD/RIE | 3 Jan 04 | 1 Jun | 30 |
| Old Mulla 5 | CP | M | GRD/RIE | 1 Nov 03 | 1 Jun | 15 |
| Old Mulla 10 | CP | M | GRD/RIE | 6 Jan 04 | 1 Jun | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 1 Jun | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | TBD | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 1 May |  |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 15 Mar | 41 towers complete/236 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | 29 Feb | 229 towers complete/293 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 2 Mar | 60 towers complete/66 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | 2 Mar | 81 towers complete/81 req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Diyala Connection | 400 | Sabotage | ME |  | 30 Apr |  |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Dibis/Irbil-Azadi/Quarqush | 132 | New Line | GRD/RIE |  | 1 Jun |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | 15 Feb |  |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 Mar |  |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| Report Date - 11 FEBRUARY 2004 |
| --- |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Power transferred from North to Middle 750 MW. |
| Power transferred from South to Middle 220 MW. |
| Baghdad | 1500 | 32117 | 1338 |
| Duhok | 80 | 1935 | 81 |
| Naynawa | 375 | 9018 | 376 |
| Tamim | 165 | 3816 | 159 |
| Salah Aldeen | 190 | 4901 | 204 |
| Anbar | 155 | 4292 | 179 |
| Dyala | 92 | 2409 | 100 |
| Babil | 110 | 2574 | 107 |
| Kirbala | 127 | 2809 | 117 |
| Najaf | 135 | 3208 | 134 |
| Kadsya | 50 | 1449 | 60 |
| Wasit | 105 | 2423 | 101 |
| Muthana | 55 | 1356 | 57 |
| Nasirya | 135 | 2827 | 118 |
| Misan | 60 | 1303 | 54 |
| Basra | 335 | 7800 | 325 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil