Daily Power System Highlights for February 15, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:  No power from Syria due to high winds affecting power lines.

Generation:

Peak Power 4070Mw, 91,541Mw hours, 7-day Avg. 4275Mw

Generators Returned to Service                                                                                     85 Mw

Daura 3                                                                                                                               65 Mw

Shuaiba 2                                                                                                                           20 Mw

Generators Unscheduled Out of Service					  656 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 2 | SP | Boiler leak | 8 |
| * Dibis 4 | SP | Boiler Leak | 8 |
| * Baiji 4 | SP | Boiler Leak | 80 |
| South Baghdad 3 | SP | Hydraulic System problems | 30 |
| South Baghdad 5 | SP | Air Heater | 30 |
| * Nassirya 1 | SP | System Cleaning | 130 |
| * Baiji 1 | CP | Line Trip | 85 |
| Baiji 2, | CP | Lubricating oil leak | 110 |
| Hilla 1 | CP | Cooling System problems | 20 |
| Hilla 2 | CP | Servo | 20 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo and Circuit breaker | 15 |
| Old Mulla 3 | CP | Principle Protector | 15 |
| New Mulla 6 | CP | Generator Defect | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service 	1016 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 4 Mar | 100 |
| Daura 3 | CP | R | GRD/RIE | 1 Mar 03 | 1 Jun | 20 |
| Daura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Daura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Daura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME | 30Dec 03 | 15 Feb | 8 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 30 Mar | 18 |
| Hartha 4 | SP | M | ME/Bechtel | 23Oct 03 | 14 Feb | 150 |
| Khor Zubayr 4 | CP | R | GRD/RIE | 20Dec03 | 14 Feb | 55 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 7 Mar | 180 |
| Najaf 2 | CP | M | GRD/RIE | 5 Dec 03 | 30 Apr | 50 |
| New Mulla 1 | CP | M | GRD/RIE | 13 Jan 04 | 1 Jun | 30 |
| Old Mulla 5 | CP | M | GRD/RIE | 1 Nov 03 | 1 Jun | 15 |
| Old Mulla 10 | CP | M | GRD/RIE | 6 Jan 04 | 1 Jun | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 1 Jun | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | TBD | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | TBD | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 1 May |  |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 22 Mar | 41 towers complete/236 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | 29 Feb | 264 towers complete/293 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 5 Mar | 68 towers complete/68 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | 20 Feb | 81 towers complete/81 req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Diyala Connection | 400 | Sabotage | ME |  | 30 Apr |  |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Dibis/Irbil-Azadi/Quarqush | 132 | New Line | GRD/RIE |  | 1 Jun |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | 15 Feb |  |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 Mar |  |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| --- | --- | --- | --- |
| Power transferred from North to Middle 800 MW. |
| Power transferred from South to Middle 220MW. |
| Baghdad | 1520 | 32973 | 1374 |
| Duhok | 50 | 1912 | 80 |
| Naynawa | 330 | 9757 | 407 |
| Tamim | 121 | 3739 | 156 |
| Salah Aldeen | 185 | 5111 | 213 |
| Anbar | 180 | 4527 | 189 |
| Dyala | 100 | 2446 | 102 |
| Babil | 110 | 2571 | 107 |
| Kirbala | 110 | 2561 | 107 |
| Najaf | 120 | 2880 | 120 |
| Kadsya | 65 | 1518 | 63 |
| Wasit | 95 | 2364 | 99 |
| Muthana | 60 | 1396 | 58 |
| Nasirya | 120 | 2710 | 113 |
| Misan | 60 | 1466 | 61 |
| Basra | 260 | 7319 | 305 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil