## A-Steam Power Stations
Report Date - 15 FEBRUARY 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 | 8 | [5 empty] | 8 | 24 | #2 boiler leakage; #3 prog maint; #4 stopped at 142 boiler leakage
Baiji | Fuel Oil | 6 | 3 | 90 |  | 75 |  |  | 95 | 260 | 500 | #2 prog maint; #4 stopped at 516 boiler leakge; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 65 |  |  |  | 65 | 180 | #3 synch at 1655; #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  | 30 |  | 30 | 60 | 200 | #1 & #2 prog maint; #3 hyd, system prob; #4 synch at 0012; #5 a/h
Mussaibe | Crude and Fuel Oil | 4 | 3 | 200 | 200 | 200 |  |  |  | 600 | 860 | #4 prog maint
Nassirya | Crude | 4 | 3 |  | 165 | 165 | 145 |  |  | 475 | 600 | #1 stopped at 800 con. Cleaning
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 35 | 80 |  | 115 | 160 | #4 one boiler in operation
Hartha | Natural Gas and Crude | 4 | 1 | 100 | [5 empty] | 100 | 300 | #4 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1683 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date - 15 FEBRUARY 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 |  |  | 125 | Gas Oil | #1 stopped at 630 line trip; #2 lub oil leak from bearing, | Musil Dam Main | 4 | 4 | 560 | 600
Quds | 2 | 2 | 135 | 160 | Gas Oil | 29 trucks | Musil Dam reg | 4 | 4 | 36 | 60 | 1000
Mosil | 12 | 10 | 68 | 150 | 23 | #1 rotor defec; #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 2 | 55 | 30 | 26 | #4 rehab | Haditha Dam | 6 | 2 | 140 | 160 | 300
Old Mulla | 12 | 6 | 70 | 128 | 430 | #1 acc gear; #2 servo; #3 prim prot; #5 prog maint; #10 prog maint; #12 needs rehab | Samarra | 3 | 2 | 42 | 55 | 400
New Mulla | 6 | 4 | 60 | 173 | 2.9 | #1 prog maint; #6 generator defect | Himrin | 2 | 2 | 42 | 21 | 130
Taji | 7 | 5 | 70 | 55 | 18 | #3 compressor; #7 needs rehab | Hindia | 4 | 4 | 5 | 5 | 115
M. Taji | 2 | 1 | 7 | 18 | 18 | #2 software | Kufa | 4 | 3 | 1 | 0 | 70
Daura | 4 | 2 | 50 | 30 | 17 | #3 needs rehab |  |  | Total | 936 | 896
Hilla | 4 | 2 | 32 | 64 | 35 | #1 cooling sys prob; #2 servo | System Generation |  | 83340 | MWh
Najaf | 3 | 2 | 95 | 129 | 34 | #2 prog maint | Syrian Line Generation |  | 942 | MWh
Khor | 4 | 3 | 80 | 80 | Natural Gas | #4 rehab | Turkey Line Generation |  | 1819 | MWh
Shuaiba | 2 | 1 | 6 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 91541 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3754 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  |  | MW
M. Dibis | 4 | 3 | 12 | 24 | Natural Gas |  | Turkey Peak Load |  | 50 | MW
Mossil East | 5 | 3 | 17 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Total Peak Load |  | 4070 | MW
Diesel |  |  | 48 |  | Gas Oil |  | Baghdad Load |  | 1520 | MW
|  | Total | 818 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 15 FEBRUARY 2004
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Power transferred from North to Middle 800 MW.
Power transferred from South to Middle 220MW.
Baghdad | 1520 | 32973 | 1374
Duhok | 50 | 1912 | 80
Naynawa | 330 | 9757 | 407
Tamim | 121 | 3739 | 156
Salah Aldeen | 185 | 5111 | 213
Anbar | 180 | 4527 | 189
Dyala | 100 | 2446 | 102
Babil | 110 | 2571 | 107
Kirbala | 110 | 2561 | 107
Najaf | 120 | 2880 | 120
Kadsya | 65 | 1518 | 63
Wasit | 95 | 2364 | 99
Muthana | 60 | 1396 | 58
Nasirya | 120 | 2710 | 113
Misan | 60 | 1466 | 61
Basra | 260 | 7319 | 305