Daily Power System Highlights for February 17, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:  Khor Zubayr 4, out of Programmed Maintenance, operational now.

Generation:

Peak Power 4266Mw, 89,315Mw hours, 7-day Avg. 4311Mw

Generators Returned to Service                                                                                335 Mw

Khor Zubayr 4                                                                                                                  55 Mw     Baiji 4, SP                                                                                                                        80 Mw

Mussaibe 2                                                                                                                    200 Mw

Generators Unscheduled Out of Service                                                             811 Mw				  876 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 2 | SP | Boiler leak | 8 |
| Dibis 4 | SP | Boiler Leak | 8 |
| * Baiji 3 | SP | Control valve closed | 80 |
| South Baghdad 5 | SP | Steam Leak | 30 |
| * South Baghdad 6 | SP | No Signal | 30 |
| Nassirya 1 | SP | System Cleaning | 130 |
| Baiji 1 | CP | Line Trip | 85 |
| Baiji 2, | CP | Lubricating oil leak | 110 |
| * Qudis 2 | CP | Fuel Shortage | 75 |
| Doura 4 | CP | Gas Pressure Low | 20 |
| Hilla 1 | CP | Cooling System problems | 20 |
| Hilla 2 | CP | Servo | 20 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 3 | SP | Gas Pressure Low | 15 |
| Mosil 4 | SP | Gas Pressure Low | 15 |
| Mosil 8 | SP | Gas Pressure Low | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo and Circuit breaker | 15 |
| * New Mulla 2 | CP | Maintenance | 30 |
| New Mulla 6 | CP | Generator Defect | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service 	961 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 4 Mar | 100 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | 1 Jun | 20 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME | 30Dec 03 | 15 Feb | 8 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 30 Mar | 18 |
| Hartha 4 | SP | M | ME/Bechtel | 23Oct 03 | 14 Feb | 150 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 7 Mar | 180 |
| Najaf 2 | CP | M | GRD/RIE | 5 Dec 03 | 30 Apr | 50 |
| New Mulla 1 | CP | M | GRD/RIE | 13 Jan 04 | 1 Jun | 30 |
| Old Mulla 5 | CP | M | GRD/RIE | 1 Nov 03 | 1 Jun | 15 |
| Old Mulla 10 | CP | M | GRD/RIE | 6 Jan 04 | 1 Jun | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 1 Jun | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | TBD | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | TBD | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 1 May | 102 towers complete/211 req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 22 Mar | 41 towers complete/236 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | 29 Feb | 278 towers complete/293 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 5 Mar | 68 towers complete/68 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | 20 Feb | 81 towers complete/81 req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Diyala Connection | 400 | Sabotage | ME |  | 30 Apr |  |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Dibis/Irbil-Azadi/Quarqush | 132 | New Line | GRD/RIE |  | 1 Jun |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | 15 Feb | 43 towers complete/43 req’d |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 May | 26 towers complete/126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| Report Date - 17 FEBRUARY 2004 |
| --- |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Power transferred from North to Middle 810 MW. |
| Power transferred from South to Middle 240 MW. |
| Baghdad | 1500 | 31691 | 1320 |
| Duhok | 82 | 1922 | 80 |
| Naynawa | 360 | 9070 | 378 |
| Tamim | 150 | 3287 | 137 |
| Salah Aldeen | 220 | 5127 | 214 |
| Anbar | 240 | 4304 | 179 |
| Dyala | 125 | 2204 | 92 |
| Babil | 95 | 2350 | 98 |
| Kirbala | 85 | 1710 | 71 |
| Najaf | 92 | 2190 | 91 |
| Kadsya | 55 | 1383 | 58 |
| Wasit | 90 | 1924 | 80 |
| Muthana | 65 | 1326 | 55 |
| Nasirya | 120 | 2834 | 118 |
| Misan | 70 | 1396 | 58 |
| Basra | 355 | 7542 | 314 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil