## A-Steam Power Stations
Report Date - 24 FEBRUARY 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 | 8 |  |  |  |  | 16 | 24 | #3 prog maint; #4 boiler leakage
Baiji | Fuel Oil | 6 | 4 | 90 |  | 85 | 80 |  | 100 | 355 | 500 | #2 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 75 |  |  |  | 75 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 1 |  |  | 20 |  |  |  | 20 | 200 | #1 & #2 prog maint; #4 stopped at 1150 boiler leakage; #5 stopped at 250 boiler leakage; #6 boiler leakage
Mussaibe | Crude and Fuel Oil | 4 | 2 |  | 200 | 200 |  |  |  | 400 | 860 | #1 boiler leakage; #4 prog maint
Nassirya | Crude | 4 | 3 | 135 | 165 |  | 75 |  |  | 375 | 600 | #3 vacuums prob; #4 stopped at 1705 vacuum prob, synch at 1900
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 85 | 90 |  | 175 | 160
Hartha | Natural Gas and Crude | 4 | 1 | 130 | [5 empty] | 130 | 300 | #4 excit. prob
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1546 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date - 24 FEBRUARY 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 130 | 125 | Gas Oil | #2 lub oil leak from bearing | Musil Dam Main | 4 | 4 | 565 | 600
Quds | 2 | 1 | 80 | 160 | Gas Oil | 24 trucks - #2 stopped at 125 fuel level low | Musil Dam reg | 4 | 3 | 23 | 60 | 1000
Mosil | 12 | 8 | 120 | 150 | 21 | #1 rotor defect; #3 synch at 1020; #5 synch at 1005; #7 & #8 transt prob; #9 rotor defect; #12 generator fault | Musil Pumping | 2 | 1 | 100 | 0
Dibis | 3 | 2 | 56 | 30 | 28 | #4 rehab | Haditha Dam | 6 | 2 | 125 | 160 | 350
Old Mulla | 12 | 7 | 111 | 128 | 30 | #1 acc. Gear; #2 servo; #5 prog maint; #10 prog maint; #11 synch at 1014; #12 needs rehab | Samarra | 3 | 3 | 48 | 55 | 420
New Mulla | 6 | 4 | 140 | 173 | 30 | #1 synch at 1413; #2 prog maint; #6 generator defect | Himrin | 2 | 2 | 44 | 21 | 160
Taji | 7 | 5 | 69 | 55 | 14 | #3 compressor; #7 needs rehab | Hindia | 4 | 4 | 5 | 5 | 120
M. Taji | 2 | 1 | 8 | 18 | 14 | #2 software | Kufa | 4 | 1 | 1 | 0 | 30
Daura | 4 | 1 | 25 | 30 | 18 | #2 prog maint; #3 needs rehab; #4 stopped at 520 c/b |  |  | Total | 911 | 896
Hilla | 4 | 2 | 35 | 64 | 28 | #1 cooling sys prob; #2 servo | System Generation |  | 80750 | MWh
Najaf | 3 | 3 | 140 | 129 | 23 |  | Syrian Line Generation |  | 1369 | MWh
Khor | 4 | 3 | 120 | 80 | Natural Gas | #2 prog maint | Turkey Line Generation |  | 944 | MWh
Shuaiba | 2 | 1 | 5 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 88490 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3629 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 4 | 12 | 24 | Natural Gas |  | Turkey Peak Load |  | 56 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 4011 | MW
Diesel |  |  | 43 |  | Gas Oil |  | Baghdad Load |  | 1300 | MW
|  | Total | 1121 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 24 FEBRUARY 2004
Power transferred from North to Middle 845 MW.
Power transferred from South to Middle 124 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1300 | 29740 | 1239
Duhok | 84 | 1303 | 54
Naynawa | 310 | 9447 | 394
Tamim | 120 | 3827 | 159
Salah Aldeen | 200 | 4837 | 202
Anbar | 185 | 4012 | 167
Dyala | 75 | 1847 | 77
Babil | 75 | 2202 | 92
Kirbala | 146 | 2657 | 111
Najaf | 156 | 2861 | 119
Kadsya | 55 | 1310 | 55
Wasit | 65 | 1871 | 78
Muthana | 59 | 1353 | 56
Nasirya | 140 | 2807 | 117
Misan | 61 | 1439 | 60
Basra | 310 | 7455 | 311