Daily Power System Highlights for February 27, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Generation:

Peak Power 4060Mw, 94,097Mw hours, 7-day Avg. 4148Mw

Generators Returned to Service      None reported

Generators Unscheduled Out of Service                                                                    958 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 4 | SP | Boiler Leak | 8 |
| South Baghdad 3 | SP | Boiler Leak | 30 |
| South Baghdad 6 | SP | Boiler Leak | 30 |
| * Doura 3 | SP | Drum Level low | 70 |
| Mussaibe 1 | SP | Boiler Leak | 200 |
| * Mussaibe 2 | SP | Thrust Bearing problem | 200 |
| * Nejibiya 5 | SP | Auxillary power Loss | 90 |
| Baiji 2, | CP | Lubricating oil leak | 110 |
| Hilla 1 | CP | Cooling System problems | 20 |
| Hilla 2 | CP | Servo | 20 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Mosil 12 | CP | Generator fault | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo | 15 |
| New Mulla 5 | CP | Inlet Gate Valve (IGV) | 30 |
| New Mulla 6 | CP | Generator Defect | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji 4 | CP | Control card | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service                                                                                  816 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 4 Mar | 100 |
| Doura 2 | CP | M | ME | 21 Feb 04 | TBD | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | 15 May | 20 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME | 30Dec 03 | 31 May | 8 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 30 Mar | 18 |
| Khor Zubayr 2 | CP | M | ME | 19 Feb 04 | TBD | 50 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 7 Mar | 180 |
| New Mulla 2 | CP | M | ME | 17 Feb04 | TBD | 30 |
| Old Mulla 5 | CP | M | GRD/RIE | 1 Nov 03 | 15 May | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | TBD | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | 31 May | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 102 towers complete/212req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 20 Apr | 45 towers complete/236 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | 7 Mar | 287 towers complete/297 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 14 Mar | 68 towers complete/68 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | 28 Feb | 81 towers complete/81req’d |
| Baghd S. – Diwaniyah | 400 | Sabotage | GRD/RIE |  | Compl. 24 Jan | 27 towers complete/27 req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 30 Apr |  |
| Dibis/Irbil-Quarqush | 132 | New Line | GRD/RIE |  | 15 May | Contractor on-site 20 Feb |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | 28 Feb | 44 towers complete/44 req’d |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 May | 26 towers complete/126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| Power transferred from North to Middle 850 MW. |
| --- |
| Power transferred from South to Middle 240 MW. |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Baghdad | 1460 |  |  |
| Duhok | 60 |  |  |
| Naynawa | 278 |  |  |
| Tamim | 123 |  |  |
| Salah Aldeen | 175 |  |  |
| Anbar | 163 |  |  |
| Dyala | 78 |  |  |
| Babil | 111 |  |  |
| Kirbala | 104 |  |  |
| Najaf | 109 |  |  |
| Kadsya | 50 |  |  |
| Wasit | 85 |  |  |
| Muthana | 53 |  |  |
| Nasirya | 122 |  |  |
| Misan | 51 |  |  |
| Basra | 320 |  |  |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil