Daily Power System Highlights for February 29, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

1. Rotor for Doura #5, SP left Doura plant today for the Siemens factory.

2. Both Doura #5 and #6, SP, successfully passed hi-pot electrical tests .

3. Qudas plant – As of 2 pm Sunday Feb 29, Unit 1 successfully changed over from gas-oil (diesel) fuel to crude oil firing, currently producing 40 Mw.

Generation:

Peak Power 4187Mw, 90,559Mw hours, 7-day Avg. 4153Mw

Generators Returned to Service                                                                                 168 Mw

Dibis 4, SP                                                                                                                         8 Mw

Doura 3, SP                                                                                                                     70 Mw

Najebia 5, SP                                                                                                                   90 Mw

Generators Unscheduled Out of Service                                                                 1025 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| * South Baghdad 4 | SP | Low Voltage | 30 |
| South Baghdad 5 | SP | Boiler Leak | 30 |
| Doura 3 | SP | Drum Level low | 70 |
| Mussaibe 1 | SP | Boiler Leak | 200 |
| Mussaibe 2 | SP | Thrust Bearing problem | 200 |
| * Hartha 4 | SP | Boiler Leak | 80 |
| Baiji 2, | CP | Lubricating oil leak | 110 |
| * Qudas 2 | CP | Fuel Level low | 80 |
| Hilla 1 | CP | Cooling System problems | 20 |
| Hilla 2 | CP | Servo | 20 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo | 15 |
| * Najaf 2 | CP | Bearing oil leak | 50 |
| New Mulla 6 | CP | Generator Defect | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji 4 | CP | Control card | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service                                                                                1166 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 4 Mar | 100 |
| Baiji 3 | SP | M | ME | 29 Feb 04 | 29 Apr | 100 |
| Doura 2 | CP | M | ME | 21 Feb 04 | TBD | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | 15 May | 20 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME | 30Dec 03 | 31 May | 8 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 30 Mar | 18 |
| Khor Zubayr 2 | CP | M | ME | 19 Feb 04 | TBD | 50 |
| Mosul 8 | CP | M | ME | 28 Feb 04 | TBD | 15 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 7 Mar | 200 |
| New Mulla 2 | CP | M | ME | 17 Feb04 | TBD | 30 |
| Old Mulla 5 | CP | M | GRD/RIE | 1 Nov 03 | 15 May | 15 |
| Old Mulla 8 | CP | M | GRD/RIE | 28 Feb 04 | 15 May | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | TBD | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | 31 May | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 102 towers complete/212req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 20 Apr | 45 towers complete/236 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | 7 Mar | 287 towers complete/297 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 14 Mar | 68 towers complete/68 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | 28 Feb | 81 towers complete/81req’d |
| Baghd S. – Diwaniyah | 400 | Sabotage | GRD/RIE |  | Compl. 24 Jan | 27 towers complete/27 req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 30 Apr |  |
| Dibis/Irbil-Quarqush | 132 | New Line | GRD/RIE |  | 15 May | Contractor on-site 20 Feb |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | 28 Feb | 44 towers complete/44 req’d |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 May | 26 towers complete/126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| Power transferred from North to Middle 810 MW. |
| --- |
| Power transferred from South to Middle 275 MW. |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Baghdad | 1470 | 29323 | 1222 |
| Duhok | 84 | 1897 | 79 |
| Naynawa | 300 | 9323 | 388 |
| Tamim | 135 | 3471 | 145 |
| Salah Aldeen | 205 | 4951 | 206 |
| Anbar | 179 | 4650 | 194 |
| Dyala | 80 | 2313 | 96 |
| Babil | 90 | 2700 | 113 |
| Kirbala | 130 | 2598 | 108 |
| Najaf | 165 | 3487 | 145 |
| Kadsya | 52 | 1483 | 62 |
| Wasit | 105 | 2218 | 92 |
| Muthana | 65 | 1386 | 58 |
| Nasirya | 135 | 2923 | 122 |
| Misan | 80 | 1496 | 62 |
| Basra | 340 | 7690 | 320 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil