## A-Steam Power Stations
Report Date - 04 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 |  |  | 8 |  |  | 16 | 24 | #2 boiler leakage; #3 prog maint
Baiji | Fuel Oil | 6 | 2 |  |  |  | 90 |  | 100 | 190 | 500 | #1 stopped at 456 H/EXE; #2 & #3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 65 |  |  |  | 65 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  | 25 |  | 30 | 30 | 85 | 200 | #1 & #2 prog maint; #4 boiler leakage
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 210 |  |  |  | 410 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 4 | 135 | 145 | 165 | 155 |  |  | 600 | 600
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 90 | 90 |  | 180 | 160
Hartha | Natural Gas and Crude | 4 | 1 | 100 |  |  | 55 |  |  | 155 | 300
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1701 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date - 04 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 130 | 125 | Gas Oil | #2 lub oil leak from bearing | Musil Dam Main | 4 | 4 | 560 | 600
Quds | 2 | 1 | 100 | 160 | Gas Oil | 32 trucks; #1 fuel pump | Musil Dam reg | 4 | 3 | 31 | 60 | 1000
Mosil | 12 | 9 | 140 | 150 | 31 | #1 & #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 25 | 30 | 25 | #4 rehab; #5 thermo coupl | Haditha Dam | 6 | 4 | 150 | 160 | 600
Old Mulla | 12 | 6 | 80 | 128 | 420 | #1 acc gear; #2 servo; #5 prog maint; #7 load gear; #8 prog maint; #12 needs rehab | Samarra | 3 | 3 | 50 | 55 | 500
New Mulla | 6 | 4 | 100 | 173 | 280 | #6 generator defect | Himrin | 2 | 2 | 50 | 21
Taji | 7 |  |  | 55 |  | #3 compressor; #4 control card + N.G.P.L.; #7 needs rehab | Hindia | 4 | 4 | 5 | 5
M. Taji | 2 |  |  | 18 |  | #2 software N.G.P.L. | Kufa | 4 | 4 | 1 | 0
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab = N.G.P.L. |  |  | Total | 957 | 896
Hilla | 4 | 2 | 30 | 64 | 31 | #1 cooling sys prob; #2 servo | System Generation |  | 76666 | MWh
Najaf | 3 | 3 | 130 | 129 | 27 |  | Syrian Line Generation |  | 1410 | MWh
Khor | 4 | 3 | 130 | 80 | Natural Gas | #2 prog maint | Turkey Line Generation |  | 2036 | MWh
Shuaiba | 2 | 1 | 5 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 85539 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3517 | MW
Petro | 4 |  |  | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 |  |  |  | Gas Oil |  | Total Peak Load |  | 3923 | MW
Diesel |  |  |  |  | Gas Oil |  | Baghdad Load |  | 1270 | MW
|  | Total | 894 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 04 MARCH 2004
Power transferred from North to Middle740MW.
Power transferred from South to Middle 250 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1270 | 27049 | 1127
Duhok | 80 | 1900 | 79
Naynawa | 270 | 9329 | 389
Tamim | 130 | 3454 | 144
Salah Aldeen | 185 | 4917 | 205
Anbar | 180 | 4894 | 204
Dyala | 94 | 2631 | 110
Babil | 95 | 2488 | 104
Kirbala | 124 | 2695 | 112
Najaf | 147 | 2942 | 123
Kadsya | 50 | 1503 | 63
Wasit | 81 | 2201 | 92
Muthana | 55 | 1407 | 59
Nasirya | 110 | 2809 | 117
Misan | 65 | 1535 | 64
Basra | 300 | 7165 | 299