## A-Steam Power Stations
Reporting Peak for 06 MARCH 2004 / Report Date - 07 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 | 8 | [5 empty] | 8 | 24 | #1 boiler leakage; #3 prog maint; #4 boiler leakage
Baiji | Fuel Oil | 6 | 2 | 90 |  |  | 80 |  | 80 | 250 | 500 | #1 synch at 0058; #2 prog maint; #4 synch at 1707 stopped at 306 FDF; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 70 |  |  |  | 70 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  | 25 | 30 | 30 | 30 | 115 | 200 | #1 & #2 prog maint; #4 boiler leakage
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 200 |  |  |  | 400 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 4 | 130 | 125 | 145 | 125 |  |  | 525 | 600
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  |  | 90 |  | 90 | 160 | #4 valve leak
Hartha | Natural Gas and Crude | 4 | 2 | 90 |  |  | 90 |  |  | 180 | 300 | #1 high furnace press
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1638 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 06 MARCH 2004 / Report Date - 07 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 100 | 125 | Gas Oil | #1 lub oil leak from bearing | Musil Dam Main | 4 | 4 | 570 | 600
Quds | 2 | 1 | 100 | 160 | Gas Oil | 25 trucks | Musil Dam reg | 4 | 3 | 26 | 60 | 1000
Mosil | 12 | 9 | 140 | 150 | 28 | #1 & #9 rotor defect; #12 needs rehab | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 2 | 50 | 30 | 28 | #2 prog maint; #6 generator defect | Haditha Dam | 6 | 4 | 165 | 160 | 450
Old Mulla | 12 | 7 | 110 | 128 | 470 | #1 acc gear; #2 servo; #5 prog maint; #12 needs rehab | Samarra | 3 | 3 | 53 | 55
New Mulla | 6 | 4 | 135 | 173 | 350 | #2 prog maint; #3 needs rehab | Himrin | 2 | 2 | 50 | 21
Taji | 7 |  |  | 55 |  | #3 compressor; #4 stopped a t 600 control card; #7 needs rehab | Hindia | 4 | 4 | 6 | 5
M. Taji | 2 |  |  | 18 |  | #2 software | Kufa | 4 | 2 | 2 | 0
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab |  |  | Total | 982 | 896
Hilla | 4 | 2 | 32 | 64 | 35 | #1 cooling sys prob; #2 servo | System Generation |  | 76840 | MWh
Najaf | 3 | 2 | 120 | 129 | 31 | #2 stopped at 1705 vib | Syrian Line Generation |  | 1306 | MWh
Khor | 4 | 4 | 148 | 80 | Natural Gas | #2 prog maint | Turkey Line Generation |  | 1660 | MWh
Shuaiba | 2 | 1 | 5 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 85233 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3506 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 62 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 50 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 3884 | MW
Diesel |  |  | 34 |  | Gas Oil |  | Baghdad Load |  | 1380 | MW
|  | Total | 1010 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 06 MARCH 2004 / Report Date - 07 MARCH 2004
Power transferred from North to Middle 810MW.
Power transferred from South to Middle 260 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1380 | 27761 | 1157
Duhok | 50 | 1736 | 72
Naynawa | 310 | 8019 | 334
Tamim | 120 | 3094 | 129
Salah Aldeen | 210 | 4914 | 205
Anbar | 195 | 4493 | 187
Dyala | 95 | 2281 | 95
Babil | 95 | 2516 | 105
Kirbala | 90 | 2220 | 93
Najaf | 139 | 2818 | 117
Kadsya | 65 | 1474 | 61
Wasit | 85 | 2175 | 91
Muthana | 58 | 1431 | 60
Nasirya | 120 | 2888 | 120
Misan | 61 | 1582 | 66
Basra | 300 | 6742 | 281