## A-Steam Power Stations
Reporting Peak for 09 MARCH 2004 / Report Date - 10 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 |  | 8 |  | 8 |  |  | 16 | 24 | #1 boiler leakage; #3 prog maint
Baiji | Fuel Oil | 6 | 3 | 85 |  |  | 85 |  | 95 | 265 | 500 | #2 & #3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 65 |  |  |  | 65 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 1 |  |  |  | 30 |  |  | 30 | 200 | #1 & #2 prog maint; #3 gen diff; #5 stopped at 2300 boiler leakage; #6 stopped 1945 F.D.F.
Mussaibe | Crude and Fuel Oil | 4 | 2 | 110 |  | 215 |  |  |  | 325 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 3 | 130 |  | 125 | 90 |  |  | 345 | 600 | #2 prog maint
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 90 | 90 |  | 180 | 160 | #4 valve leak
Hartha | Natural Gas and Crude | 4 | 1 | 100 | [5 empty] | 100 | 300 | #4 boiler leak
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1326 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 09 MARCH 2004 / Report Date - 10 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 95 | 125 | Gas Oil | #1 lub oil leak from bearing; #2 heavy oil | Musil Dam Main | 4 | 4 | 605 | 600
Quds | 2 | 2 | 150 | 160 | Gas Oil | 33 trucks | Musil Dam reg | 4 | 3 | 27 | 60 | 1000
Mosil | 12 | 9 | 135 | 150 | 30 | #1 & #9 rotor defect; #11 H.P. | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 2 | 54 | 30 | 31 | #4 rehab | Haditha Dam | 6 | 3 | 180 | 160 | 600
Old Mulla | 12 | 8 | 115 | 128 | 500 | #1 acc gear; #2 servo; #5 & #6 synch; #12 needs rehab | Samarra | 3 | 3 | 67 | 55
New Mulla | 6 | 4 | 130 | 173 | 320 | #2 prog maint; #6 generator defect | Himrin | 2 | 2 | 50 | 21
Taji | 7 |  |  | 55 |  | #3 compressor; #4 stopped at 600 control card N.G. press low; #7 needs rehab | Hindia | 4 | 4 | 6 | 5
M. Taji | 2 |  |  | 18 |  | #2 software | Kufa | 4 | 3 | 1 | 0
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab NG press low |  |  | Total | 1046 | 896
Hilla | 4 | 3 | 45 | 64 | 32 | #2 synch at 1640; #3 turbine blades, prog maint | System Generation |  | 79408 | MWh
Najaf | 3 | 3 | 130 | 129 | 29 | #2 vib | Syrian Line Generation |  | 1358 | MWh
Khor | 4 | 3 | 120 | 80 | Natural Gas | #4 gen prot | Turkey Line Generation |  | 2020 | MWh
Shuaiba | 2 | 1 | 5 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 82786 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas |  | System Peak Load |  | 3546 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 2 | 10 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 3952 | MW
Diesel |  |  | 53 |  | Gas Oil |  | Baghdad Load |  | 1442 | MW
|  | Total | 1063 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 09 MARCH 2004 / Report Date - 10 MARCH 2004
Power transferred from North to Middle 850 MW.
Power transferred from South to Middle 120 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1442 | 29942 | 1248
Duhok | 80 | 1923 | 80
Naynawa | 300 | 8358 | 348
Tamim | 150 | 3517 | 147
Salah Aldeen | 195 | 5139 | 214
Anbar | 180 | 4533 | 189
Dyala | 110 | 2264 | 94
Babil | 185 | 3454 | 144
Kirbala | 93 | 2113 | 88
Najaf | 110 | 2452 | 102
Kadsya | 45 | 1238 | 52
Wasit | 90 | 2079 | 87
Muthana | 45 | 1400 | 58
Nasirya | 130 | 2968 | 124
Misan | 65 | 1556 | 65
Basra | 275 | 6595 | 275