Daily Power System Highlights for March 15, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS: Hartha 1 and 4, SP, operating at reduced load due to load flow problems.  Hilla 1,2, and 4 CP,  offline approx 6 hours for the connection of new mobile.

We will continue to see decreased power as we enter into the spring maintenance period.  Sabotage will continue to have unanticipated and detrimental effects on power output.

Generation:

Peak Power 4123Mw, 90,087Mw hours, 7-day Avg. 4064Mw

Generators Returned to Service:                                                                                     90 Mw

South Baghdad 6                                                                                                                 30 Mw

Hilla, 1,2,4                                                                                                                            60 Mw

Generators Unscheduled Out of Service                                                                594 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| * Dibis 1 | SP | Pilot Light | 8 |
| Dibis 2 | SP | Boiler Leak | 8 |
| Dibis 4 | SP | Fuel Filters | 8 |
| South Baghdad 3 | SP | Generator Differential | 30 |
| South Baghdad 5 | SP | Air Heater | 30 |
| * Mussaibe 1 | SP | Burner problems | 200 |
| Baiji 2 | CP | Heavy Oil commissioning | 110 |
| Khor Zubayr 4 | CP | Generator Protector | 50 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Mosil 11 | CP | Hydraulic Pressure | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo | 15 |
| New Mulla 6 | CP | Generator Defect | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji 4 | CP | Control card | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service                                                                                1256 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 2 | SP | M | Bechtel | 2 Jan 04 | 22 Mar | 100 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 1 May | 100 |
| Doura 2 | CP | M | ME | 21 Feb 04 | 15 May | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | 15 May | 20 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 30 Apr | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 31May | 100 |
| Dibis 3 | SP | M | ME | 30Dec 03 | 31 May | 8 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 1 May | 18 |
| Hilla 3 | CP | M | ME | 9 Mar 04 | TBD | 20 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 15 May | 200 |
| Nassirya 2 | SP | M | ME | 9 Mar 04 | 15 Apr | 150 |
| New Mulla 2 | CP | M | ME | 17 Feb04 | TBD | 30 |
| Old Mulla 8 | CP | M | GRD/RIE | 28 Feb 04 | 15 May | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | 31 May | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 102 towers complete/212req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 15 Apr | 216 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | 297 towers complete/297 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 31 Mar | 68 towers complete/68 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | ME |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 30 May |  |
| Dibis/Irbil-Quarqush | 132 | New Line | GRD/RIE |  | 15 May | Notice to proceed issued 12 Mar |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Omara-Burzegan | 132 | Looting | ME |  | 1 May | 26 towers complete/126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

None reported today

Distribution:

| Report Date -15 MARCH 2004 |
| --- |
| Power transferred from North to Middle 870 MW. |
| Power transferred from South to Middle 205 MW. |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Baghdad | 1425 | 30024 | 1251 |
| Duhok | 85 | 1912 | 80 |
| Naynawa | 340 | 8669 | 361 |
| Tamim | 125 | 3420 | 143 |
| Salah Aldeen | 220 | 5161 | 215 |
| Anbar | 210 | 4728 | 197 |
| Dyala | 112 | 2521 | 105 |
| Babil | 104 | 2647 | 110 |
| Kirbala | 85 | 1944 | 81 |
| Najaf | 95 | 2351 | 98 |
| Kadsya | 100 | 2082 | 87 |
| Wasit | 108 | 2342 | 98 |
| Muthana | 68 | 1508 | 63 |
| Nasirya | 132 | 2783 | 116 |
| Misan | 70 | 1544 | 64 |
| Basra | 325 | 6335 | 264 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil