## A-Steam Power Stations
Reporting Peak for 15 MARCH 2004 / Report Date - 16 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 7 | 8 |  |  |  |  | 15 | 24 | #1 synch at 1720; #2 synch at 1105; #3 prog maint; #4 fuel filters
Baiji | Fuel Oil | 6 | 3 | 95 |  |  | 90 |  | 85 | 270 | 500 | #2 & #3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | 1 |  |  | 65 |  |  |  | 65 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  |  | 30 | 30 | 60 | 200 | #1 & #2 prog maint; #3 gen earth; #4 stopped at 910 s.v prob; #5 synch at 845
Mussaibe | Crude and Fuel Oil | 4 | 2 | 185 |  | 215 |  |  |  | 400 | 860 | #1 synch at 1617; #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 3 | 130 |  | 135 | 150 |  |  | 415 | 600 | #2 prog maint
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 55 | 60 |  | 115 | 160 | load flow problem
Hartha | Natural Gas and Crude | 4 | 2 | 75 |  |  | 70 |  |  | 145 | 300 | load flow problem
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1485 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 15 MARCH 2004 / Report Date - 16 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 90 | 125 | Gas Oil | #1 heavy oil; #2 lub oil | Musil Dam Main | 4 | 4 | 620 | 600
Quds | 2 | 2 | 100 | 160 | Gas Oil | 30 trucks | Musil Dam reg | 4 | 3 | 26 | 60 | 1100
Mosil | 12 | 9 | 140 | 150 | 30 | #1 & #9 rotor defect; #11 H.P. | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 2 | 50 | 30 | 26 | #4 rehab | Haditha Dam | 6 | 3 | 210 | 160 | 1250
Old Mulla | 12 | 8 | 121 | 128 | 420 | #1 acc gear; #2 servo; #8 VIB; #12 needs rehab | Samarra | 3 | 3 | 78 | 55 | 780
New Mulla | 6 | 4 | 140 | 173 | 2.8 | #2 prog maint; #6 generator defect | Himrin | 2 | 1 | 50 | 21 | 200
Taji | 7 |  |  | 55 |  | #2 compressor; #7 needs rehab. No control card N.G. press low | Hindia | 4 | 4 | 5 | 5 | 160
M. Taji | 2 |  |  | 18 |  | #2 sotfware + NGPL | Kufa | 4 | 3 | 1 | 0 | 60
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab NG press low |  |  | Total | 1100 | 896
Hilla | 4 | 3 | 58 | 64 | 30 | #3 prog maint | System Generation |  | 82300 | MWh
Najaf | 3 | 3 | 140 | 129 | 28 |  | Syrian Line Generation |  | 1318 | MWh
Khor | 4 | 3 | 75 | 80 | Natural Gas | #2 prog maint | Turkey Line Generation |  | 1938 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas | #1 prog maint | Total Generation |  | 90938 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3725 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas | #2 vib | Turkey Peak Load |  | 70 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 2 | 2 |  | Gas Oil |  | Total Peak Load |  | 4121 | MW
Diesel |  |  | 52 |  | Gas Oil |  | Baghdad Load |  | 1500 | MW
|  | Total | 1006 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 15 MARCH 2004 / Report Date - 16 MARCH 2004
Power transferred from North to Middle 850 MW.
Power transferred from South to Middle 170 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1500 | 30904 | 1288
Duhok | 70 | 1851 | 77
Naynawa | 350 | 8518 | 355
Tamim | 140 | 3376 | 141
Salah Aldeen | 230 | 5199 | 217
Anbar | 205 | 4902 | 204
Dyala | 110 | 2624 | 109
Babil | 120 | 2569 | 107
Kirbala | 80 | 1919 | 80
Najaf | 117 | 2585 | 108
Kadsya | 65 | 1618 | 67
Wasit | 90 | 2067 | 86
Muthana | 90 | 1829 | 76
Nasirya | 120 | 2702 | 113
Misan | 70 | 1560 | 65
Basra | 305 | 6641 | 277