## A-Steam Power Stations
Reporting Peak for 22 MARCH 2004 / Report Date - 23 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 | 8 |  |  |  |  | 16 | 24 | #3 FWP; #4 prog maint
Baiji | Fuel Oil | 6 | 2 |  | 125 |  |  |  | 85 | 210 | 500 | #1 & #3 prog maint; #4 starting; #5 forced outage; #6 limited to crack in furnace wall
Daura | Fuel Oil | 4 | 1 |  |  | 65 |  |  |  | 65 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 1 | [5 empty] | 30 | 30 | 200 | #1, #2, #3 prog maint; #4 stopped at 1320 boiler leakage to be start tomorrow; #5 a/h to be start afternoon
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 225 |  |  |  | 425 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 2 | 140 |  | 150 |  |  |  | 290 | 600 | #2 prog maint; #4 IDF defect - to be start tomorrow
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  |  | 90 |  | 90 | 160 | #4 oil leakage to be start after 48 hrs
Hartha | Natural Gas and Crude | 4 | 2 | 55 |  |  | 150 |  |  | 205 | 300 | load flow problem
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1331 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 22 MARCH 2004 / Report Date - 23 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 2 | 170+55 | 125 | Gas Oil | #2 synch at 1350+3 mobil gass unit at peak load | Musil Dam Main | 4 | 4 | 620 | 600
Quds | 2 | 2 | 200 | 160 | Gas Oil | 46 trucks | Musil Dam reg | 4 | 3 | 30 | 60 | 1100
Mosil | 12 | 7 | 50 | 150 | 13 | #1 rotor defect; #2 prog maint - NGPL; #8 stopped at 1710; #11 HP | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 2 | 50 | 30 | 28 | #4 rehab | Haditha Dam | 6 | 4 | 216 | 160 | 2100
Old Mulla | 12 | 6 | 96 | 128 | 420 | #1 acc gear; #2 servo; #5 inlet valve; #8 VIB; #9 & #10 Cp explosion; #12 needs rehab | Samarra | 3 | 3 | 80 | 55 | 780
New Mulla | 6 | 5 | 170 | 173 | 2.9 | #6 generator defect sch at 15/5 | Himrin | 2 | 2 | 45 | 21 | 200
Taji | 7 |  |  | 55 |  | #3 compressor; #7 needs rehab - no control card NG press low | Hindia | 4 | 3 | 4 | 5 | 160
M. Taji | 2 |  |  | 18 |  | #2 software + NGPL | Kufa | 4 |  |  | 0
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab NG press low |  |  | Total | 1105 | 896
Hilla | 4 | 4 | 59 | 64 | 31 | #3 synch at 1214 | System Generation |  | 78213 | MWh
Najaf | 3 | 3 | 137 | 129 | 29 |  | Syrian Line Generation |  | 1373 | MWh
Khor | 4 | 3 | 125 | 80 | Natural Gas | #2 prog maint; #4 synch at 1341 | Turkey Line Generation |  | 1927 | MWh
Shuaiba | 2 | 2 | 7 | 20 | Natural Gas |  | Total Generation |  | 86940 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas |  | System Peak Load |  | 3610 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 2 | 10 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 4016 | MW
Diesel |  |  | 48 |  | Gas Oil |  | Baghdad Load |  | 1380 | MW
|  | Total | 973 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 22 MARCH 2004 / Report Date - 23 MARCH 2004
Power transferred from North to Middle 780 MW.
Power transferred from South to Middle 85 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Baghdad | 1380 | 29948 | 1248
Duhok | 80 | 1924 | 80
Naynawa | 335 | 8723 | 363
Tamim | 140 | 3253 | 136
Salah Aldeen | 210 | 5339 | 222
Anbar | 205 | 5052 | 211
Dyala | 100 | 2626 | 109
Babil | 110 | 2715 | 113
Kirbala | 94 | 2144 | 89
Najaf | 115 | 2690 | 112
Kadsya | 70 | 1516 | 63
Wasit | 90 | 2178 | 91
Muthana | 59 | 1474 | 61
Nasirya | 120 | 2721 | 113
Misan | 65 | 1510 | 63
Basra | 275 | 5985 | 248