## A-Steam Power Stations
Reporting Peak for 23 MARCH 2004 / Report Date - 24 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 | 8 | [5 empty] | 8 | 24 | #2 stopped at 2058 NGPL; #3 FWP; #4 prog maint
Baiji | Fuel Oil | 6 | 3 |  | 135 |  | 80 |  | 90 | 305 | 500 | #1 & #3 prog maint; #4 synch at 1327; #5 forced outage; #6 limited to crack in furnace wall
Daura | Fuel Oil | 4 | 1 |  |  | 70 |  |  |  | 70 | 180 | #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  |  | 30 | 30 | 60 | 200 | #1, #2, #3 prog maint; #4 boiler leakage; #5 synch at 2159
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 225 |  |  |  | 425 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 2 | 140 |  | 140 |  |  |  | 280 | 600 | #2 prog maint; #4 IDF defect - to be started tomorrow
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  |  | 90 |  | 90 | 160 | #4 oil leakage to be started at 48 hrs
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 140 |  |  | 140 | 300 | load flow problem
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1378 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 23 MARCH 2004 / Report Date - 24 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 82 | 125 | Gas Oil | #2 stopped at 1730 test | Musil Dam Main | 4 | 4 | 620 | 600
Quds | 2 | 2 | 80 | 160 | Gas Oil | 45 trucks | Musil Dam reg | 4 | 3 | 30 | 60 | 1100
Mosil | 12 | 8 | 130 | 150 | 27 | #1 rotor defect; #2 prog maint; #8 synch at 1130; #9 rotor defect; #11 HP | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 |  |  | 30 | 28 | #4 rehab; #5 stopped at 2125 NGPL at 23/3; #6 stopped at 2108 NGPL at 23/3 | Haditha Dam | 6 | 4 | 215 | 160 | 2100
Old Mulla | 12 | 5 | 61 | 128 | 430 | #1 acc gear; #5 inlet valve; #6 stopped at 2025 HET; #8 VIB; #9 & #10 CT explosion; #12 needs rehab | Samarra | 3 | 3 | 80 | 55 | 780
New Mulla | 6 | 5 | 172 | 173 | 2.9 | #6 generator defet (sch 15/5) | Himrin | 2 | 2 | 40 | 21 | 200
Taji | 7 |  |  | 55 |  | #3 compressor; #7 needs rehab - no control card + NGPL | Hindia | 4 | 4 | 3 | 5 | 160
M. Taji | 2 | 1 | 4 | 18 | GO | #2 software + NGPL | Kufa | 4 |  |  | 0 | low level
Daura | 4 |  |  | 30 |  | #2 prog maint; #3 needs rehab + NGPL |  |  | Total | 1098 | 896
Hilla | 4 | 4 | 73 | 64 | 29 |  | System Generation |  | 77977 | MWh
Najaf | 3 | 3 | 135 | 129 | 29 |  | Syrian Line Generation |  | 1405 | MWh
Khor | 4 | 3 | 96 | 80 | Natural Gas | #2 prog maint | Turkey Line Generation |  | 1981 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas |  | Total Generation |  | 86790 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas |  | System Peak Load |  | 3609 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 82 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Total Peak Load |  | 4017 | MW
Diesel |  |  | 49 |  | Gas Oil |  | Baghdad Load |  | 1370 | MW
|  | Total | 922 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 23 MARCH 2004 / Report Date - 24 MARCH 2004
Power transferred from North to Middle 780 MW.
Power transferred from South to Middle 70 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1370 | 28355 | 1181 | 1452
Duhok | 82 | 1904 | 79 | 109
Naynawa | 330 | 8495 | 354 | 485
Tamim | 135 | 3643 | 152 | 201
Salah Aldeen | 210 | 5165 | 215 | 267
Anbar | 225 | 4932 | 206 | 259
Dyala | 124 | 2605 | 109 | 139
Babil | 95 | 2696 | 112 | 143
Kirbala | 98 | 2265 | 94 | 113
Najaf | 114 | 2702 | 113 | 129
Kadsya | 60 | 1576 | 66 | 83
Wasit | 95 | 2168 | 90 | 124
Muthana | 65 | 1447 | 60 | 72
Nasirya | 120 | 2792 | 116 | 131
Misan | 66 | 1568 | 65 | 76
Basra | 300 | 6226 | 259 | 259