Daily Power System Highlights for March 26, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

We will continue to see decreased power as we enter into the spring maintenance period.  Sabotage will continue to have unanticipated and detrimental effects on power output.

Generation:

Peak Power 4102Mw, 87,700Mw hours, 7-day Avg. 4098Mw

Generators Returned to Service:   None reported

Generators Unscheduled Out of Service   (17)                                                       478 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 3 | SP | Feed water pump | 8 |
| South Baghdad 4 | SP | Boiler Leak | 30 |
| Najebia 4 | SP | Oil Leak | 90 |
| Baiji 2 | CP | Fuel Valve trouble | 110 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Mosil 11 | CP | Hydraulic Pressure | 15 |
| Dibis 6 | CP | Natural Gas Pressure Low | 30 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo | 15 |
| Old Mulla 5 | CP | Inlet Valve | 15 |
| Old Mulla 8 | CP | Vibrations | 15 |
| Old Mulla 9,10 | CP | Transformer damage | 30 |
| New Mulla 6 | CP | Generator Defect | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji 4 | CP | Control card | 15 |
| Taji Mobile, 2 | CP | Software problem | 15 |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service   (21)                                                                       1468 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | TBD | 21 Mar 04 | 21 May | 100 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 1 May | 100 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | 30 Apr | 8 |
| Doura 2 | CP | M | ME | 21 Feb 04 | 15 May | 20 |
| Doura 3 | CP | R | TBD | 1 Mar 03 |  | 20 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 30 May | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 30 Jun | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 1 Sep | 110 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 23 May | 100 |
| Khor Zubayr 2 | CP | M | GRD/RIE | 15 Mar 04 | 21 May | 50 |
| Mosil 2 | CP | M | ME | 21 Mar 04 | TBD | 15 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 15 May | 200 |
| Nassirya 2 | SP | M | ME | 9 Mar 04 | 15 Apr | 150 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | 31 May | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 18 May | 20 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 102 towers complete/212req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 15 Apr | 246 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | 297 towers complete/297 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 31 Mar | 68 towers complete/68 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 30 May |  |
| Dibis/Erbil-Qara Qosh | 132 | New Line | GRD/RIE |  | 15 May | Contractor mobilized |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 15 Jun | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Al Amarah-Burzulgan | 132 | Looting | GRD-RIE |  | 15 Jun | 26 towers complete /126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:  None reported today

Distribution: No Report Today

| Report Date -26 MARCH 2004 |
| --- |
| Power transferred from North to Middle 850 MW. |
| Power transferred from South to Middle 140 MW. |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW |
| Baghdad |  |  |  |
| Duhok |  |  |  |
| Naynawa |  |  |  |
| Tamim |  |  |  |
| Salah Aldeen |  |  |  |
| Anbar |  |  |  |
| Dyala |  |  |  |
| Babil |  |  |  |
| Kirbala |  |  |  |
| Najaf |  |  |  |
| Kadsya |  |  |  |
| Wasit |  |  |  |
| Muthana |  |  |  |
| Nasirya |  |  |  |
| Misan |  |  |  |
| Basra |  |  |  |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil