## A-Steam Power Stations
Reporting Peak for 28 MARCH 2004 / Report Date - 29 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 3 | 8 | 8 | 8 |  |  |  | 24 | 24 | #4 prog maint
Baiji | Fuel Oil | 6 | 2 |  | 120 |  |  |  | 80 | 200 | 500 | #1 & #3 prog maint; #4 stopped at 0631 a/h; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3 prog maint; #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  |  | 30 | 30 | 30 | 90 | 200 | #1, #2, #3 prog maint
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 220 |  |  |  | 420 | 860 | #2 prog maint; #4 prog maint
Nassirya | Crude | 4 | 3 | 135 |  | 140 | 100 |  |  | 375 | 600 | #2 prog maint; #4 synch at 1355
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 90 | 90 |  | 180 | 160 | #4 boiler #4 in operation; #5 boiler (5) 2345 in operation
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 140 |  |  | 140 | 300 | load flow problem
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1429 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 28 MARCH 2004 / Report Date - 29 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 90 | 125 | Gas Oil | #2 fuel oil pipe | Musil Dam Main | 4 | 3 | 460 | 600
Quds | 2 | 2 | 150 | 160 | Gas Oil | 39 trucks | Musil Dam reg | 4 | 3 | 33 | 60 | 1100
Mosil | 12 | 8 | 120 | 150 | 23 | #1 rotor defect; #2 CB - Prog maint; #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 25 | 30 | 32 | #4 rehab; #6 starting diesel | Haditha Dam | 6 | 4 | 200 | 160 | 1000
Old Mulla | 12 | 5 | 75 | 128 | 520 | #1 acc gear; #6 HET; #9 VIB; #9, #10 CT explosion; #12 needs rehab | Samarra | 3 | 3 | 78 | 55 | 780
New Mulla | 6 | 4 | 145 | 173 | 320 | #3 stopped at 1705 Hyd press; #6 generator defect (sch at 15/5) | Himrin | 2 | 2 | 32 | 21 | 150
Taji | 7 | 3 | 50 | 55 | 19 | #1 GEN vib; #3 compressor; #4 stopped lub oil; #7 needs rehab (NGPL) | Hindia | 4 | 2 | 2 | 5
M. Taji | 2 |  |  | 18 | G.O. | #2 software (NGPL) | Kufa | 4 |  |  | 0
Daura | 4 | 2 | 40 | 30 | 18 | #1 = 17 synch; #2 prog maint; #3 needs rehab (NGPL) |  |  | Total | 915 | 896
Hilla | 4 | 4 | 60 | 64 | 24 |  | System Generation |  | 77243 | MWh
Najaf | 3 | 3 | 120 | 129 | 21 |  | Syrian Line Generation |  | 1326 | MWh
Khor | 4 | 2 | 100 | 80 | Natural Gas | #2 prog maint; #4 stopped at 0842 cooling system | Turkey Line Generation |  | 1993 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas |  | Total Generation |  | 85989 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas |  | System Peak Load |  | 3449 | MW
Petro | 4 |  |  | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 57 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 84 | MW
Mossil East | 5 | 2 | 10 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Total Peak Load |  | 3856 | MW
Diesel |  |  | 47 |  | Gas Oil |  | Baghdad Load |  | 1265 | MW
|  | Total | 1048 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 28 MARCH 2004 / Report Date - 29 MARCH 2004
Power transferred from North to Middle 850 MW.
Power transferred from South to Middle 70 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1265 | 27772 | 1157 | 1356
Duhok | 84 | 1928 | 80 | 107
Naynawa | 385 | 8792 | 366 | 487
Tamim | 149 | 3337 | 139 | 185
Salah Aldeen | 248 | 5082 | 212 | 265
Anbar | 200 | 4449 | 185 | 247
Dyala | 94 | 2502 | 104 | 143
Babil | 93 | 2660 | 111 | 145
Kirbala | 75 | 1973 | 82 | 110
Najaf | 90 | 2492 | 104 | 128
Kadsya | 60 | 1441 | 60 | 85
Wasit | 80 | 2089 | 87 | 122
Muthana | 65 | 1404 | 59 | 76
Nasirya | 130 | 2879 | 120 | 129
Misan | 65 | 1492 | 62 | 77
Basra | 265 | 5932 | 247 | 247