## A-Steam Power Stations
Reporting Peak for 29 MARCH 2004 / Report Date - 30 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 3 | 8 | 8 | 8 |  |  |  | 24 | 24 | #4 prog maint
Baiji | Fuel Oil | 6 | 2 | [5 empty] | 85 | 85 | 500 | #1 prog maint; #2 1207 stopped - hydrogen leak; #3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3 & #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  |  | 30 |  | 30 | 60 | 200 | #1, #2, #3 prog maint; #5 1925 stopped boiler leak
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 220 |  |  |  | 420 | 860 | #1 0555 trip EHG; #2 & #4 prog maint
Nassirya | Crude | 4 | 3 | 130 |  | 125 | 130 |  |  | 385 | 600 | #2 prog maint
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 90 | 90 |  | 180 | 160
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 140 |  |  | 140 | 300 | load flow problem
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1294 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 29 MARCH 2004 / Report Date - 30 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 |  |  | 125 | Gas Oil | #1 1640 tripped service transf | Musil Dam Main | 4 | 3 | 460 | 600
Quds | 2 | 2 | 210 | 160 | Gas Oil | 39 trucks | Musil Dam reg | 4 | 3 | 28 | 60 | 1100
Mosil | 12 | 6 | 95 | 150 | 23 | #1 rotor defect; #2 CB - prog maint; #6 reverse power; #9 rotor defect | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 2 | 45 | 30 | 29 | #4 rehab; #6 starting diesel | Haditha Dam | 6 | 4 | 200 | 160 | 1000
Old Mulla | 12 | 6 | 90 | 128 | 480 | #1 acc gear; #6 HET; #8 VIB; #9 & #10 CT explosion; #12 needs rehab | Samarra | 3 | 3 | 70 | 55 | 700
New Mulla | 6 | 4 | 110 | 173 | 300 | #1 HGT; #3 stopped at 1705 hyd. Press; #6 generator defect (sch at 15/5) | Himrin | 2 | 2 | 33 | 21 | 125
Taji | 7 | 4 | 50 | 55 | 18 | #1 GEN vib; #3 compressor; #4 stopped lub oil; #7 needs rehab | Hindia | 4 | 2 | 2 | 5
M. Taji | 2 | 1 | 8 | 18 |  | #2 software | Kufa | 4 |  |  | 0
Daura | 4 | 2 | 45 | 30 | 18 | #1 = 17 synch; #2 prog maint; #3 needs rehab |  |  | Total | 903 | 896
Hilla | 4 | 4 | 65 | 64 | 23 |  | System Generation |  | 75034 | MWh
Najaf | 3 | 3 | 120 | 129 | 20 |  | Syrian Line Generation |  | 1189 | MWh
Khor | 4 | 2 | 110 | 80 | Natural Gas | #2 prog maint; #4 stopped at 0842 cooling system | Turkey Line Generation |  | 1930 | MWh
Shuaiba | 2 | 1 | 6 | 20 | Natural Gas |  | Total Generation |  | 83580 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas |  | System Peak Load |  | 3498 | MW
Petro | 4 |  |  | 0 | Natural Gas | #2 vib | Syria Peak Load |  | 53 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
Mossil East | 5 | 2 | 15 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 266 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Total Peak Load |  | 3897 | MW
Diesel |  |  | 45 |  | Gas Oil |  | Baghdad Load |  | 1200 | MW
|  | Total | 1026 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 29 MARCH 2004 / Report Date - 30 MARCH 2004
Power transferred from North to Middle 750 MW.
Power transferred from South to Middle 150 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1200 | 27124 | 1130 | 1405
Duhok | 80 | 1900 | 79 | 104
Naynawa | 320 | 8169 | 340 | 483
Tamim | 125 | 3327 | 139 | 189
Salah Aldeen | 225 | 5176 | 216 | 259
Anbar | 210 | 4591 | 191 | 233
Dyala | 100 | 2403 | 100 | 141
Babil | 118 | 2592 | 108 | 141
Kirbala | 115 | 2194 | 91 | 109
Najaf | 120 | 2489 | 104 | 127
Kadsya | 65 | 1565 | 65 | 89
Wasit | 95 | 2056 | 86 | 124
Muthana | 65 | 1387 | 58 | 74
Nasirya | 120 | 2737 | 114 | 126
Misan | 75 | 1456 | 61 | 77
Basra | 300 | 6045 | 252 | 252