Daily Power System Highlights for March 31, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

We will continue to see decreased power as we enter into the spring maintenance period.  Sabotage will continue to have unanticipated and detrimental effects on power output.

Generation:

Peak Power 3881Mw, 81,868Mw hours, 7-day Avg. 3986Mw

Generators Returned to Service:                                                                                   110 Mw

Baiji 4, SP                                                                                                                             80 Mw

New Mulla 1                                                                                                                          30 Mw

Generators Unscheduled Out of Service   (23)                                                       814 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Baiji 2 | SP | Hydrogen leak | 120 |
| Baiji 1 | CP | Fuel Pressure Low | 90 |
| * Baiji 6 | SP | High water consumption | 85 |
| Baiji 2 | CP | Vibrations | 110 |
| * South Baghdad 4 | SP | Boiler Leak | 30 |
| South Baghdad 5 | SP | Boiler Leak | 30 |
| * Doura 4 | CP | Gas pressure low | 20 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| * Mosil 12 | CP | Transformer problem | 15 |
| Dibis 6 | CP | Converting to Diesel | 30 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 2 | CP | Servo | 15 |
| Old Mulla 5 | CP | High exhaust temperature | 15 |
| Old Mulla 6 | CP | High exhaust temperature | 15 |
| Old Mulla 8 | CP | Vibrations | 15 |
| Old Mulla 9,10 | CP | Transformer damage | 30 |
| New Mulla 3 | CP | Hydraulic Pressure | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji 1 | CP | Vibrations | 15 |
| Taji 4 | CP | Lubrication oil leak | 15 |
| M. Taji 2 | CP | Software | 15 |
| Khor Zubayr 4 | CP | Cooling System problem | 50 |

RED – Denotes out of service since last report

Generators Scheduled Out of Service   (25)                                                                       1638 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | TBD | 21 Mar 04 | 21 May | 100 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 1 May | 100 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | 30 Apr | 8 |
| Doura 2 | CP | M | ME | 21 Feb 04 | 15 May | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | TBD | 20 |
| Doura 3 | SP | M | ME | 18 Mar 04 | 18 May | 65 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 30 May | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 30 Jun | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 12 May | 30 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 23 May | 100 |
| Khor Zubayr 2 | CP | R | GRD/RIE | 15 Mar 04 | 15 Jun | 50 |
| Mosil 2 | CP | M | GRD/RIE | 21 Mar 04 | 15 May | 15 |
| Mosil 11 | CP | M | ME | 30 Mar 04 | TBD | 15 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 4 Apr | 200 |
| Nassirya 1 | SP | M | ME | 30 Mar 04 | 15 May | 130 |
| Nassirya 2 | SP | M | ME | 9 Mar 04 | 15 Apr | 150 |
| New Mulla 6 | CP | R | GRD/RIE | 28 Mar 04 | 15 May | 30 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | 31 May | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 18 May | 20 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 102 towers complete/212req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 15 Apr | 246 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | 297 towers complete/297 req’d |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | 31 Mar | 68 towers complete/68 req’d |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 30 May |  |
| Dibis/Erbil-Qara Qosh | 132 | New Line | GRD/RIE |  | 15 May | Contractor mobilized |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 15 Jun | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Al Amarah-Burzulgan | 132 | Looting | GRD-RIE |  | 15 Jun | 26 towers complete /126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:  None reported today

Distribution:

| Power transferred from North to Middle 785 MW. |  |
| --- | --- |
| Power transferred from South to Middle 80 MW. |  |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW |
| Baghdad | 1240 | 26758 | 1115 | 1438 |
| Duhok | 80 | 1907 | 79 | 104 |
| Naynawa | 330 | 7463 | 311 | 473 |
| Tamim | 130 | 2952 | 123 | 177 |
| Salah Aldeen | 230 | 4947 | 206 | 257 |
| Anbar | 220 | 4594 | 191 | 256 |
| Dyala | 86 | 2064 | 86 | 134 |
| Babil | 95 | 2372 | 99 | 136 |
| Kirbala | 86 | 2041 | 85 | 111 |
| Najaf | 100 | 2376 | 99 | 130 |
| Kadsya | 71 | 1391 | 58 | 84 |
| Wasit | 85 | 1981 | 83 | 130 |
| Muthana | 60 | 1313 | 55 | 78 |
| Nasirya | 130 | 2727 | 114 | 133 |
| Misan | 68 | 1414 | 59 | 80 |
| Basra | 275 | 6006 | 250 | 250 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil