## A-Steam Power Stations
Reporting Peak for 30 MARCH 2004 / Report Date - 31 MARCH 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 3 | 8 | 8 | 8 |  |  |  | 24 | 24 | #4 prog maint
Baiji | Fuel Oil | 6 | 1 |  |  |  | 75 |  |  | 75 | 500 | #1 prog maint; #2 hydrogen leak; #3 prog maint; #4 synch at 1627; #5 forced outage; #6 stopped at 1912 high water consump
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3 & #4 prog maint; #5 & #6 rehab
South Baghdad | Fuel Oil | 6 | 1 | [5 empty] | 30 | 30 | 200 | #1, #2, #3 prog maint; #4 stopped at 235 boiler leakage; #5 starting
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 220 |  |  |  | 420 | 860 | #1 synch at 1132; #2 & #4 prog maint
Nassirya | Crude | 4 | 2 |  |  | 130 | 130 |  |  | 260 | 600 | #1 & #2 prog maint
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 70 | 65 |  | 135 | 160
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 130 |  |  | 130 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1074 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 30 MARCH 2004 / Report Date - 31 MARCH 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 |  |  | 125 | Gas Oil | #1 stopped at 2355 FP prob; #2 vib | Musil Dam Main | 4 | 4 | 618 | 600
M. Baiji | 8 | 4 | 90 |  | Gas Oil |  | Musil Dam reg | 4 | 4 | 40 | 60 | 1100
Quds | 2 | 2 | 150 | 160 | Gas Oil | 40 trucks | Musil Pumping | 2 | 1 | 110 | 0
Mosil | 12 | 7 | 105 | 150 | 16 | #1 rotor defect; #2 prog maint; #9 rotor defect; #11 prog maint; #12 transf | Haditha Dam | 6 | 4 | 220 | 160 | 1000
Dibis | 3 | 1 | 30 | 30 | 30 | #4 rehab; #6 starting diesel | Samarra | 3 | 3 | 70 | 55 | 700
Old Mulla | 12 | 5 | 65 | 128 | 440 | #1 acc gear; #5 stopped at 1512 HET; #6 HET; #8 VIB; #9 & 10 CP explosion; #12 needs rehab | Himrin | 2 | 2 | 36 | 21 | 125
New Mulla | 6 | 5 | 158 | 173 | 3.4 | #1 synch at 1005; #6 generator defect (sch at 15/5) (NGPL) | Hindia | 4 | 2 | 2 | 5 | 60
Taji | 7 | 3 | 48 | 55 | 13 | #1 GEN vib; #3 compressor; #4 lub oil; #7 needs rehab (NGPL) | Kufa | 4 |  |  | 0
M. Taji | 2 | 1 | 4 | 18 | Gas Oil | #2 software (NGPL) |  |  | Total | 1096 | 896
Daura | 4 | 1 | 10 | 30 | 13 | #2 prog maint; #3 needs rehab; #4 stopped at 1900 (NGPL) | System Generation |  | 73338 | MWh
Hilla | 4 | 4 | 65 | 64 | 24 |  | Syrian Line Generation |  | 1215 | MWh
Najaf | 3 | 3 | 130 | 129 | 21 |  | Turkey Line Generation |  | 1888 | MWh
Khor | 4 | 3 | 100 | 80 | Natural Gas | #2 prog maint | Total Generation |  | 81868 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas |  | System Peak Load |  | 3475 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas |  | Syria Peak Load |  | 60 | MW
Petro | 4 |  |  | 0 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
M. Dibis | 4 | 2 | 9 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 3 | 16 | 0 | Gas Oil |  | Total Peak Load |  | 3881 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Baghdad Load |  | 1240 | MW
Diesel |  |  | 19 |  | Gas Oil
|  | Total | 1006 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 30 MARCH 2004 / Report Date - 31 MARCH 2004
Power transferred from North to Middle 785 MW.
Power transferred from South to Middle 80 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1240 | 26758 | 1115 | 1438
Duhok | 80 | 1907 | 79 | 104
Naynawa | 330 | 7463 | 311 | 473
Tamim | 130 | 2952 | 123 | 177
Salah Aldeen | 230 | 4947 | 206 | 257
Anbar | 220 | 4594 | 191 | 256
Dyala | 86 | 2064 | 86 | 134
Babil | 95 | 2372 | 99 | 136
Kirbala | 86 | 2041 | 85 | 111
Najaf | 100 | 2376 | 99 | 130
Kadsya | 71 | 1391 | 58 | 84
Wasit | 85 | 1981 | 83 | 130
Muthana | 60 | 1313 | 55 | 78
Nasirya | 130 | 2727 | 114 | 133
Misan | 68 | 1414 | 59 | 80
Basra | 275 | 6006 | 250 | 250