Daily Power System Highlights for April 9, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

We will continue to see decreased power as we enter into the spring maintenance period.

Generation:

Peak Power 3857Mw, 80,328Mw hours, 7-day Avg. 3763Mw

Generators Returned to Service:   None Reported

Generators Unscheduled Out of Service   (15)                                                             318 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 2 | SP | Excitor Problem | 8 |
| South Baghdad 5 | SP | Hydrogen test | 30 |
| Baiji Mobile, 1,2,3,4 | CP | No Fuel | 100 |
| Doura 1 | CP | Natural Gas Pressure low | 15 |
| Doura 4 | CP | Natural Gas Pressure low | 15 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 2 | CP | Hydraulic Pressure Low | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 5 | CP | Primary Protector | 15 |
| Old Mulla 6 | CP | High exhaust temperature | 15 |
| Old Mulla 8 | CP | Vibrations | 15 |
| Taji 3, | CP | Compressor | 15 |
| Taji 5 | CP | Excitor problem | 15 |
| M. Taji 2 | CP | Software | 15 |

RED – Denotes out of service since last report

Generators Scheduled Out of Service   (27)                                                                       1918 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | TBD | 21 Mar 04 | 21 May | 100 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 1 May | 100 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | 30 Apr | 8 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | TBD | 20 |
| Doura 3 | SP | M | ME | 18 Mar 04 | 18 May | 65 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 20 Jun | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 20 Jul | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 12 May | 30 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 23 May | 100 |
| Khor Zubayr 1 | CP | M | ME | 4 Apr 04 | TBD | 50 |
| Khor Zubayr 2 | CP | R | GRD/RIE | 15 Mar 04 | 15 Jun | 50 |
| Mosil 11 | CP | M | ME | 2 Apr 04 | TBD | 15 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 30 Apr | 200 |
| Nassirya 1 | SP | M | ME | 30 Mar 04 | 15 May | 130 |
| Nassirya 2 | SP | M | ME | 9 Mar 04 | 15 Apr | 150 |
| Nassirya 3 | SP | M | ME | 31 Mar 04 | 15 Apr | 130 |
| Nassirya 4 | SP | M | ME | 31 Mar 04 | 15 Apr | 130 |
| New Mulla 6 | CP | R | GRD/RIE | 28 Mar 04 | 15 May | 30 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Shuaiba 1 | CP | M | ME | 14 Feb 04 | 31 May | 20 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 18 May | 20 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Taji 6 | CP | M | ME | 2 Apr 04 | TBD | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 102 towers complete/212req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | 15 Apr | 246 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | MoE completing PLC work |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | Complete | In service 31 March |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 15 Jun |  |
| Dibis/Erbil-Qara Qosh | 132 | New Line | GRD/RIE |  | 15 May | Contractor mobilized |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 15 Jun | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Al Amarah-Burzulgan | 132 | Looting | GRD-RIE |  | 15 Jun | 26 towers complete /126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

Distribution:

| Power transferred from North to Middle 1100 MW. |  |
| --- | --- |
| Power transferred from South to Middle 150 MW. |  |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW |
| Baghdad |  |  |  |  |
| Duhok |  |  |  |  |
| Naynawa |  |  |  |  |
| Tamim |  |  |  |  |
| Salah Aldeen |  |  |  |  |
| Anbar |  |  |  |  |
| Dyala |  |  |  |  |
| Babil |  |  |  |  |
| Kirbala |  |  |  |  |
| Najaf |  |  |  |  |
| Kadsya |  |  |  |  |
| Wasit |  |  |  |  |
| Muthana |  |  |  |  |
| Nasirya |  |  |  |  |
| Misan |  |  |  |  |
| Basra |  |  |  |  |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil