## A-Steam Power Stations
Reporting Peak for 14 APRIL 2004 / Report Date - 15 APRIL 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 3 | 8 | 8 | 8 |  |  |  | 24 | 24 | #2 synch at 1640; #4 prog maint
Baiji | Fuel Oil | 6 | 3 |  | 100 |  | 80 |  | 100 | 280 | 500 | #1, #3 prog maint; #4 synch at 2326; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3, #4 prog maint; #5, #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  |  | 30 | 30 | 30 | 90 | 200 | #1, #2, #3 prog maint; #5 synch at 935
Mussaibe | Crude and Fuel Oil | 4 | 2 | 205 |  | 225 |  |  |  | 430 | 860 | #2, #4 prog maint
Nassirya | Crude | 4 | [7 empty] | 0 | 600 | #1, #2 prog maint - shutdown till 4/15
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 85 | 90 |  | 175 | 160
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 150 |  |  | 150 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1149 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 14 APRIL 2004 / Report Date - 15 APRIL 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 |  |  | 125 | Gas Oil | #1 filter cleaning; #2 stopped at 2330 high winding temp | Musil Dam Main | 4 | 4 | 600 | 600
M. Baiji | 8 |  |  |  | Gas Oil |  | Musil Dam reg | 4 | 4 | 40 | 60 | 600
Quds | 2 | 2 | 183 | 160 | Gas Oil | 35 trucks | Musil Pumping | 2 | 1 | 110 | 0
Mosil | 12 | 9 | 138 | 150 | 28 | #1 rotor defect; #3 power supp prob; #9 rotor defect; #11 synch at 1910 | Haditha Dam | 6 | 4 | 230 | 160 | 500
Dibis | 3 | 2 | 45 | 30 | 27 | #4 rehab | Samarra | 3 | 3 | 54 | 55 | 630
Old Mulla | 12 | 6 | 90 | 128 | 540 | #1 acc gear; #6 HET; #7 gen vib; #8 vib; #10 stopped at 2259 vib; #12 needs rehab | Himrin | 2 | 2 | 36 | 21 | 150
New Mulla | 6 | 5 | 154 | 173 | 2.7 | #6 generator defect (prog maint 5/15) | Hindia | 4 | 4 | 6 | 5 | 140
Taji | 7 | 4 | 56 | 55 | 17 | #3 compressor; #5 excit prob; #6 prog main; #7 needs rehab | Kufa | 4 | 2 | 1 | 0 | 30
M. Taji | 2 |  |  | 18 | Gas Oil | #2 software |  |  | Total | 1077 | 896
Daura | 4 | 2 | 31 | 30 | 16 | #1 prog maint; #3 needs rehab | System Generation |  | 66151 | MWh
Hilla | 4 | 4 | 68 | 64 | 22 | #5 synch at the peak load | Syrian Line Generation |  | 1362 | MWh
Najaf | 3 | 3 | 120 | 129 | 21 |  | Turkey Line Generation |  | 1921 | MWh
Khor | 4 | 2 | 90 | 80 | Natural Gas | #1, #2 prog maint; #4 synch at 1715 | Total Generation |  | 74861 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas | #2 prog maint | System Peak Load |  | 3364 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas |  | Syria Peak Load |  | 56 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Turkey Peak Load |  | 80 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 3 | 17 | 0 | Gas Oil |  | Total Peak Load |  | 3766 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Baghdad Load |  | 1385 | MW
Diesel |  |  | 63 |  | Gas Oil
|  | Total | 1080 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 14 APRIL 2004 / Report Date - 15 APRIL 2004
Power transferred from North to Middle 900 MW.
Power transferred from South to Middle - 150 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1385 | 22224 | 926 | 1465
Duhok | 80 | 1901 | 79 | 115
Naynawa | 280 | 6867 | 286 | 511
Tamim | 115 | 2985 | 124 | 190
Salah Aldeen | 180 | 4734 | 197 | 260
Anbar | 180 | 4187 | 174 | 244
Dyala | 70 | 1642 | 68 | 138
Babil | 90 | 1920 | 80 | 144
Kirbala | 85 | 2145 | 89 | 107
Najaf | 85 | 2238 | 93 | 132
Kadsya | 87 | 1928 | 80 | 135
Wasit | 58 | 1323 | 55 | 91
Muthana | 67 | 1379 | 57 | 86
Nasirya | 95 | 2346 | 98 | 128
Misan | 64 | 1407 | 59 | 85
Basra | 330 | 5857 | 244 | 244