Daily Power System Highlights for April 19, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS: Nassirya 3and 4 synchronizing with the system, not producing at capacity now.  Shuaiba 2 returned from programmed maintenance.

We will continue to see decreased power as we progress through the spring maintenance period.

Generation:

Peak Power 3496Mw, 75, 542Mw hours, 7-day Avg. 3602Mw

Turkish Region Average Generation 162.9 Mw (not included in Peak Power)

Generators Returned to Service:   (8)                                                                             290 Mw

South Baghdad 5                                                                                                                 30 Mw

Nassirya 3                                                                                                                            60 Mw

Nassirya 4                                                                                                                          100 Mw

Baiji Mobile, 1,2,3                                                                                                                75 Mw

Mosil 11                                                                                                                               15 Mw

Shuaiba 2                                                                                                                            10 Mw

Generators Unscheduled Out of Service   (21)                                                              818 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 2 | SP | Boiler Leak | 8 |
| South Baghdad 6 | SP | Boiler leak | 30 |
| * Hartha 4 | SP | Furnace leak | 180 |
| Baiji 1 | CP | Filter Cleaning | 85 |
| Baiji Mobile, 4 | CP | No Fuel Filters | 100 |
| * Khor Zubayr 4 | CP | Flame loss | 50 |
| * Khor Zubayr 1 | CP | Bleeder valve problem | 50 |
| Qudas 2 | CP | Control card problems | 90 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 2 | CP | Load Gear Oil leak | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 1 | CP | Acc Gear | 15 |
| Old Mulla 6 | CP | High exhaust temperature | 15 |
| Old Mulla 7 | CP | Generator Vibrations | 15 |
| Old Mulla 9 | CP | Load gear problems | 15 |
| Old Mulla 10 | CP | Vibrations | 15 |
| New Mulla 3 | CP | Load gear oil leak | 30 |
| New Mulla 4 | CP | Load gear oil leak | 30 |
| Taji 3, | CP | Compressor | 15 |
| Taji 5 | CP | Excitor problem | 15 |
| M. Taji 2 | CP | Software | 15 |

RED – Denotes out of service since last report

Generators Scheduled Out of Service   (24)                                                                       1608 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | TBD | 21 Mar 04 | 15 May | 100 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 20 Apr | 100 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | 30 Apr | 8 |
| Doura 4 | CP | M | ME | 14 Apr 04 | TBD | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | TBD | 20 |
| Doura 3 | SP | M | ME | 18 Mar 04 | 18 May | 65 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 20 Jun | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 20 Jul | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 12 May | 30 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 23 May | 100 |
| Khor Zubayr 2 | CP | R | GRD/RIE | 15 Mar 04 | 15 Jun | 50 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Mussaibe 4 | SP | M | ME | 7 Feb 04 | 30 Apr | 200 |
| Nassirya 1 | SP | M | ME | 30 Mar 04 | 15 May | 130 |
| Nassirya 2 | SP | M | ME | 9 Mar 04 | 15 Apr | 150 |
| New Mulla 6 | CP | R | GRD/RIE | 28 Mar 04 | 15 May | 30 |
| Old Mulla 8 | CP | M | ME | 17 Apr 04 | TBD | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| South Baghdad 1 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 18 May | 20 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Taji 6 | CP | M | ME | 2 Apr 04 | TBD | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 102 towers complete/212req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | Complete | 246 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | MoE completing PLC work |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | Complete | Operational |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 15 Jun |  |
| Dibis/Erbil-Qara Qosh | 132 | New Line | GRD/RIE |  | 15 May | Contractor mobilized |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 15 Jun | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Al Amarah-Burzulgan | 132 | Looting | GRD-RIE |  | 15 Jun | 26 towers complete /126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

Distribution:

| Power transferred from North to Middle 900 MW. |  |
| --- | --- |
| Power transferred from South to Middle -200 MW. |  |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW |
| Baghdad | 1190 | 24186 | 1008 | 1439 |
| Duhok | 80 | 1918 | 80 | 113 |
| Naynawa | 270 | 6480 | 270 | 526 |
| Tamim | 120 | 2991 | 125 | 177 |
| Salah Aldeen | 210 | 4673 | 195 | 246 |
| Anbar | 175 | 4199 | 175 | 227 |
| Dyala | 70 | 1625 | 68 | 132 |
| Babil | 90 | 1974 | 82 | 140 |
| Kirbala | 65 | 1936 | 81 | 104 |
| Najaf | 145 | 2311 | 96 | 127 |
| Kadsya | 50 | 1291 | 54 | 88 |
| Wasit | 80 | 1836 | 77 | 124 |
| Muthana | 55 | 1280 | 53 | 74 |
| Nasirya | 90 | 2422 | 101 | 118 |
| Misan | 65 | 1558 | 65 | 83 |
| Basra | 250 | 6011 | 250 | 262 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil