Daily Power System Highlights for April 21, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS: We should begin to see a gradual climb in generation as units return from maintenance.

Generation:

Peak Power 3894Mw, 78,749Mw hours, 7-day Avg. 3731Mw

Kurdish Region Average Generation 168.1Mw (not included in Peak Power)

Generators Returned to Service:   (3)                                                                             73 Mw

Dibis 1, SP                                                                                                                                  8 Mw

Old Mulla 10                                                                                                                              15 Mw

Khor Zubayr 4                                                                                                                           50 Mw

Generators Unscheduled Out of Service   (19)                                                             656 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Dibis 2 | SP | Boiler Leak | 8 |
| * Dibis 3 | SP | Tripped-Ground/ Differential | 8 |
| South Baghdad 5 | SP | Boiler leak | 30 |
| South Baghdad 6 | SP | Boiler Leak | 30 |
| Mussaibe 4 | SP | Drum Level low | 200 |
| Baiji 1 | CP | Filter | 85 |
| Baiji Mobile, 4 | CP | No Fuel Filters | 100 |
| * Hilla 5 | CP | Testing | 15 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 2 | CP | Load Gear Oil leak | 15 |
| Mosil 8 | CP | Reverse Power | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 6 | CP | High exhaust temperature | 15 |
| Old Mulla 9 | CP | Load gear problems | 15 |
| New Mulla 4 | CP | Load gear oil leak | 30 |
| * Shaieba 2 | CP | Vibrations | 15 |
| Taji 3, | CP | Compressor | 15 |
| Taji 5 | CP | High Exhaust Temperature | 15 |
| M. Taji 2 | CP | Software | 15 |

RED – Denotes out of service since last report

Generators Scheduled Out of Service   (25)                                                                       1438 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | TBD | 21 Mar 04 | 15 May | 100 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 20 Apr | 100 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | 30 Apr | 8 |
| Doura 4 | CP | M | ME | 14 Apr 04 | TBD | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | TBD | 20 |
| Doura 3 | SP | M | ME | 18 Mar 04 | 18 May | 65 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 20 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 20 Jun | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 20 Jul | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 12 May | 30 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 23 May | 100 |
| Khor Zubayr 2 | CP | R | GRD/RIE | 15 Mar 04 | 15 Jun | 50 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Nassirya 1 | SP | M | ME | 30 Mar 04 | 15 May | 130 |
| Nassirya 2 | SP | M (Leak in water line) | ME | 9 Mar 04 | 24 Apr | 150 |
| New Mulla 6 | CP | R | GRD/RIE | 28 Mar 04 | 15 May | 30 |
| Old Mulla 1 | CP | M | ME | 17 Apr 04 | TBD | 15 |
| Old Mulla 2 | CP | M | ME | 17 Apr 04 | TBD | 15 |
| Old Mulla 8 | CP | M | ME | 17 Apr 04 | TBD | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| South Baghdad 1 | SP | M (Awaiting parts) | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 2 | SP | M (Awaiting Parts) | ME | 12 Feb 04 | 12 Apr | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 18 May | 20 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| Taji 6 | CP | M | ME | 2 Apr 04 | TBD | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 129 towers complete/216req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | Loading | 246 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | 23 Apr Operational |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | Complete | Operational |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 15 Jun |  |
| Dibis/Erbil-Qara Qosh | 132 | New Line | GRD/RIE |  | 15 May | Contractor mobilized |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 30 Jun | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Al Amarah-Burzulgan | 132 | Looting | GRD-RIE |  | 25 Jun | 26 towers complete /126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

Distribution:

| Power transferred from North to Middle 770 MW. |  |
| --- | --- |
| Power transferred from South to Middle 100 MW. |  |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW |
| Baghdad | 1210 | 26125 | 1089 | 1307 |
| Duhok | 80 | 1890 | 79 | 137 |
| Naynawa | 300 | 7493 | 312 | 436 |
| Tamim | 140 | 3086 | 129 | 172 |
| Salah Aldeen | 195 | 4485 | 187 | 228 |
| Anbar | 210 | 4135 | 172 | 211 |
| Dyala | 99 | 2378 | 99 | 128 |
| Babil | 125 | 2437 | 102 | 127 |
| Kirbala | 105 | 2153 | 90 | 99 |
| Najaf | 117 | 2429 | 101 | 108 |
| Kadsya | 95 | 1630 | 68 | 83 |
| Wasit | 65 | 1974 | 82 | 111 |
| Muthana | 63 | 1439 | 60 | 73 |
| Nasirya | 95 | 2693 | 112 | 127 |
| Misan | 65 | 1548 | 65 | 73 |
| Basra | 300 | 6340 | 264 | 265 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil