## A-Steam Power Stations
Reporting Peak for 24 APRIL 2004 / Report Date - 25 APRIL 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 | 8 | [5 empty] | 8 | 24 | #2 stopped at 1259 speed gov; #3 gen earth; #4 prog maint
Baiji | Fuel Oil | 6 | 3 |  | 90 |  | 90 |  | 100 | 280 | 500 | #1, 3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3, #4 prog maint; #5, #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  | 30 |  | 30 | 60 | 200 | #1, #2, #3 prog maint; #5 stopped at 247 BL; #6 synch at 1010
Mussaibe | Crude and Fuel Oil | 4 | 3 | 200 |  | 200 | 180 |  |  | 580 | 860 | #2 prog maint
Nassirya | Crude | 4 | 1 |  |  | 100 |  |  |  | 100 | 600 | #1 prog maint; #2 stopped at 1805 station shut down; #3 synch at 0047; #4 stopped at 1855 gen damage
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 70 |  |  | 70 | 160 | #5 starting
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 90 |  |  | 90 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1188 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 24 APRIL 2004 / Report Date - 25 APRIL 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 95 | 125 | Gas Oil | #2 C Ch test | Musil Dam Main | 4 | 4 | 600 | 600
M. Baiji | 8 | 3 | 70 |  | Gas Oil |  | Musil Dam reg | 4 | 3 | 35 | 60 | 350
Quds | 2 | 1 | 100 | 160 | Gas Oil | 29 trucks - #2 stopped at 1800 bearing prob | Musil Pumping | 2 | 1 | 110 | 0
Mosil | 12 | 7 | 115 | 150 | 31 | #1, #2 TF No. Excit; #7 prog maint; #8 synch at 1625; #9 TF No Excit | Haditha Dam | 6 | 4 | 240 | 160 | 500
Dibis | 3 | 2 | 45 | 30 | 30 | #4 TF | Samarra | 3 | 3 | 55 | 55 | 560
Old Mulla | 12 | 6 | 95 | 128 | 480 | #1, #2 TF; #8 prog maint; #9 stopped at 2044 Aut vol reg | Himrin | 2 | 2 | 35 | 21 | 135
New Mulla | 6 | 4 | 130 | 173 | 3.2 | #4 oil sys prob; #6 TF | Hindia | 4 | 4 | 5 | 5 | 135
Taji | 7 |  |  | 55 | 7 | #1, #2 NGPL; #3 TF; #4 NGPL; #5 HET; #6 prog maint | Kufa | 4 | 2 | 1 | 0 | 60
M. Taji | 2 |  |  | 18 | Gas Oil | #2 software |  |  | Total | 1081 | 896
Daura | 4 |  |  | 30 | 6 | #1, #2 NGPL; #3 needs rehab; #4 prog maint | System Generation |  | 67227 | MWh
Hilla | 4 | 4 | 68 | 64 | 23 | #5 synch at 1400 til 2200 | Syrian Line Generation |  | 1100 | MWh
Najaf | 3 | 3 | 125 | 129 | 22 |  | Turkey Line Generation |  | 1929 | MWh
Khor | 4 | 2 | 65 | 80 | Natural Gas | #2 prog maint; #4 starting | Total Generation |  | 75693 | MWh
Shuaiba | 2 |  |  | 20 | Natural Gas | #1 starting; #2 vib | System Peak Load |  | 3076 | MW
M. Shuaiba | 2 | 1 | 10 |  | Natural Gas |  | Syria Peak Load |  | 60 | MW
Petro | 4 | 3 | 9 | 0 | Natural Gas | #2 synch at 1145 | Turkey Peak Load |  | 80 | MW
M. Dibis | 4 | 3 | 16 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 1 | 2 | 0 | Gas Oil |  | Total Peak Load |  | 3482 | MW
Hmam/Zafranya | 7 |  | 50 |  | Gas Oil |  | Baghdad Load |  | 1280 | MW
Diesel |  |  |  |  | Gas Oil
|  | Total | 995 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 24 APRIL 2004 / Report Date - 25 APRIL 2004
Power transferred from North to Middle 820 MW.
Power transferred from South to Middle 50 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1280 | 26350 | 1098 | 1355
Duhok | 80 | 1890 | 79 | 115
Naynawa | 325 | 7519 | 313 | 503
Tamim | 145 | 3111 | 130 | 196
Salah Aldeen | 210 | 4527 | 189 | 246
Anbar | 186 | 4194 | 175 | 238
Dyala | 80 | 2041 | 85 | 135
Babil | 80 | 2269 | 95 | 141
Kirbala | 75 | 1988 | 83 | 112
Najaf | 89 | 2264 | 94 | 129
Kadsya | 40 | 1299 | 54 | 86
Wasit | 70 | 2093 | 87 | 116
Muthana | 40 | 1347 | 56 | 77
Nasirya | 25 | 1777 | 74 | 126
Misan | 30 | 1335 | 56 | 84
Basra | 265 | 5728 | 239 | 245