## A-Steam Power Stations
Reporting Peak for 25 APRIL 2004 / Report Date - 26 APRIL 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 | 8 |  |  |  |  | 16 | 24 | #2 synch 925; #3 gen earth; #4 prog maint
Baiji | Fuel Oil | 6 | 3 |  | 95 |  | 90 |  | 100 | 285 | 500 | #1, #3 prog maint; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3, #4 prog maint; #5, #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  | 30 |  | 25 | 55 | 200 | #1, #2, #3 prog maint; #5 BL
Mussaibe | Crude and Fuel Oil | 4 | 3 | 200 |  | 200 | 190 |  |  | 590 | 860 | #2 prog maint
Nassirya | Crude | 4 | 3 |  | 150 | 140 | 130 |  |  | 420 | 600 | #1 prog maint; #2 synch at 1155; #4 synch at 2145
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 75 |  |  | 75 | 160 | #5 starting
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 150 |  |  | 150 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1591 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 25 APRIL 2004 / Report Date - 26 APRIL 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 90 | 125 | Gas Oil | #2 C Ch test | Musil Dam Main | 4 | 4 | 600 | 600
M. Baiji | 8 | 3 | 60 |  | Gas Oil |  | Musil Dam reg | 4 | 4 | 25 | 60 | 350
Quds | 2 | 1 | 40 | 160 | Gas Oil | 26 trucks - #2 bearing prob | Musil Pumping | 2 | 1 | 110 | 0
Mosil | 12 | 8 | 120 | 150 | 30 | #1, #2 TF; #3 synch at 1826; #7 prog maint; #9 TF | Haditha Dam | 6 | 4 | 200 | 160 | 400
Dibis | 3 | 2 | 40 | 30 | 31 | #4 TF | Samarra | 3 | 3 | 59 | 55 | 560
Old Mulla | 12 | 6 | 85 | 128 | 510 | #1, #2 TF; #8 prog maint; #9 aut vol reg; #12 TF | Himrin | 2 | 2 | 35 | 21 | 135
New Mulla | 6 | 4 | 120 | 173 | 3.2 | #1, #2 NGPL; #3 TF; #4 NGPL; #5 HET; #6 prog maint; #7 TF | Hindia | 4 | 4 | 5 | 5 | 135
Taji | 7 |  |  | 55 |  | #2 software | Kufa | 4 | 2 | 1 | 0 | 60
M. Taji | 2 |  |  | 18 | Gas Oil | #1, #2 NGPL; #3 needs rehab; #4 prog maint |  |  | Total | 1035 | 896
Daura | 4 |  |  | 30 |  | #5 synch at 1400 til 2200 | System Generation |  | 68120 | MWh
Hilla | 4 | 4 | 67 | 64 | 22 | #2 prog maint; #4 synch at 828 | Syrian Line Generation |  | 1335 | MWh
Najaf | 3 | 3 | 125 | 129 | 21 | #1 starting; #2 synch at 1400 | Turkey Line Generation |  | 1881 | MWh
Khor | 4 | 3 | 137 | 80 | Natural Gas |  | Total Generation |  | 76763 | MWh
Shuaiba | 2 | 1 | 2 | 20 | Natural Gas | #2 stopped at 830 | System Peak Load |  | 3523 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas |  | Syria Peak Load |  | 60 | MW
Petro | 4 |  |  | 0 | Natural Gas |  | Turkey Peak Load |  | 82 | MW
M. Dibis | 4 | 3 | 9 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 3 | 15 | 0 | Gas Oil |  | Total Peak Load |  | 3931 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Baghdad Load |  | 1350 | MW
Diesel |  |  | 55 |  | Gas Oil
|  | Total | 967 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 25 APRIL 2004 / Report Date - 26 APRIL 2004
Power transferred from North to Middle 930 MW.
Power transferred from South to Middle 180 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1350 | 25121 | 1047 | 1369
Duhok | 82 | 1929 | 80 | 116
Naynawa | 350 | 7138 | 297 | 500
Tamim | 145 | 3086 | 129 | 181
Salah Aldeen | 220 | 4230 | 176 | 241
Anbar | 200 | 4029 | 168 | 231
Dyala | 90 | 1844 | 77 | 131
Babil | 115 | 2061 | 86 | 135
Kirbala | 85 | 1884 | 79 | 111
Najaf | 115 | 2049 | 85 | 122
Kadsya | 65 | 1274 | 53 | 87
Wasit | 100 | 1967 | 82 | 114
Muthana | 60 | 1262 | 53 | 75
Nasirya | 120 | 2141 | 89 | 116
Misan | 65 | 1275 | 53 | 78
Basra | 215 | 4687 | 195 | 208