Daily Power System Highlights for April 27, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:  Starting to see the increase in generation as units return from maintenance.

Generation:

Peak Power 4374Mw, 82,958Mw hours, 7-day Avg. 3961Mw

Generators Returned to Service:   (5)                                                                            250 Mw

South Baghdad 5                                                                                                                  30 Mw

Najebia 5                                                                                                                               80 Mw

Qudas 2                                                                                                                                95 Mw

Old Mulla 9                                                                                                                           15  Mw

New Mulla 4                                                                                                                          30 Mw

Generators Unscheduled Out of Service   (14)                                                             360 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| * South Baghdad 4 | SP | Low hydraulic pressure | 30 |
| Baiji 1 | CP | Testing | 85 |
| Baiji Mobile, 4 | CP | No Fuel Filters | 25 |
| Doura 1,2 | CP | No gas pressure | 40 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 2 | CP | Load Gear Oil leak | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| * Old Mulla 7 | CP | High exhaust temp | 15 |
| Shuaiba 1 | CP | Under Frequency | 15 |
| Shuaiba 2 | CP | Vibrations | 15 |
| Taji 1,2 | CP | No gas pressure | 45 |
| Taji 3, | CP | Compressor | 15 |
| Taji 5 | CP | High Exhaust Temp | 15 |
| M. Taji 2 | CP | Software | 15 |

RED – Denotes out of service since last report

Generators Scheduled Out of Service   (30)                                                                       1437 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | ME | 21 Mar 04 | 21 May | 100 |
| Baiji 2 | SP | M | ME | 26 Apr 04 | 29 Apr | 95 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 1 May | 100 |
| Dibis 1 | SP | M | ME | 26 Apr 04 | 1 May | 8 |
| Dibis 2 | SP | M | ME | 26 Apr 04 | 1 May | 8 |
| Dibis 3 | SP | M | ME | 26 Apr 04 | 1 May | 8 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | 30 Apr | 8 |
| Doura 4 | CP | M | ME | 14 Apr 04 | 31 May | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | 15 May | 20 |
| Doura 3 | SP | M | ME | 18 Mar 04 | 18 May | 65 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 30 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 20 Jun | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 20 Jul | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 12 May | 30 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 24 May | 100 |
| Khor Zubayr 2 | CP | R | GRD/RIE | 15 Mar 04 | 3 Jul | 50 |
| Mosil 7 | CP | M | ME | 24 Apr 04 | TBD | 15 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Nassirya 1 | SP | M | ME | 30 Mar 04 | 15 May | 130 |
| New Mulla 6 | CP | R | GRD/RIE | 28 Mar 04 | 15 May | 30 |
| Old Mulla 1 | CP | M | ME | 17 Apr 04 | 15 May | 15 |
| Old Mulla 2 | CP | M | ME | 17 Apr 04 | 15 May | 15 |
| Old Mulla 8 | CP | M | ME | 17 Apr 04 | 23 Apr | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| South Baghdad 1 | SP | M (Awaiting parts) | ME | 12 Feb 04 | TBD | 30 |
| South Baghdad 2 | SP | M (Awaiting Parts) | ME | 12 Feb 04 | TBD | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 18 May | 20 |
| Taji 4 | CP | M | ME | 21 Apr 04 | 15 JUL | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 JUL | 15 |
| Taji 6 | CP | M | ME | 2 Apr 04 | 26 May | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 129 towers complete/216req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | Loading | 246 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | 23 Apr Operational |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | Complete | Operational |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 15 Jun |  |
| Dibis/Erbil-Qara Qosh | 132 | New Line | GRD/RIE |  | 15 May | Contractor mobilized |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 30 Jun | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | 15 Jun | Contract Awarded 24 Mar |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Al Amarah-Burzulgan | 132 | Looting | GRD-RIE |  | 25 Jun | 26 towers complete /126 req’d |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

Distribution:

| Power transferred from North to Middle 1000 MW. |  |
| --- | --- |
| Power transferred from South to Middle 220 MW. |  |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW |
| Baghdad | 1500 | 28319 | 1180 | 1393 |
| Duhok | 80 | 1891 | 79 | 112 |
| Naynawa | 400 | 7632 | 318 | 506 |
| Tamim | 160 | 3283 | 137 | 187 |
| Salah Aldeen | 225 | 4803 | 200 | 253 |
| Anbar | 210 | 4006 | 167 | 220 |
| Dyala | 130 | 2067 | 86 | 141 |
| Babil | 115 | 2240 | 93 | 134 |
| Kirbala | 115 | 2058 | 86 | 108 |
| Najaf | 130 | 2233 | 93 | 127 |
| Kadsya | 80 | 1583 | 66 | 85 |
| Wasit | 110 | 2030 | 85 | 120 |
| Muthana | 60 | 1312 | 55 | 77 |
| Nasirya | 120 | 2550 | 106 | 123 |
| Misan | 65 | 1359 | 57 | 79 |
| Basra | 320 | 2962 | 248 | 253 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil