Daily Power System Highlights for April 28, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:  Starting to see the increase in generation as units return from maintenance.

Generation:

Peak Power 4251Mw, 82,283Mw hours, 7-day Avg. 4012Mw

Generators Returned to Service:   (3)                                                                            130 Mw

South Baghdad 4                                                                                                                    30 Mw

Baiji 1, CP                                                                                                                               85 Mw

Shuaiba 1                                                                                                                                15 Mw

Generators Unscheduled Out of Service   (12)                                                             260 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Baiji Mobile, 4 | CP | Fuel Filters | 25 |
| * Dibis 5 | CP | Turbine vibrations | 30 |
| Doura 1,2 | CP | No gas pressure | 40 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 2 | CP | Load Gear Oil leak | 15 |
| Mosil 9 | CP | Rotor Defect | 15 |
| Old Mulla 7 | CP | High exhaust temp | 15 |
| Shuaiba 2 | CP | Vibrations | 15 |
| Taji 1,2 | CP | No gas pressure | 45 |
| Taji 3, | CP | Compressor | 15 |
| Taji 5 | CP | High Exhaust Temp | 15 |
| M. Taji 2 | CP | Software | 15 |

RED – Denotes out of service since last report

Generators Scheduled Out of Service   (30)                                                                       1437 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | ME | 21 Mar 04 | 21 May | 100 |
| Baiji 2 | SP | M | ME | 26 Apr 04 | 29 Apr | 95 |
| Baiji 3 | SP | M | Bechtel | 29 Feb 04 | 1 May | 100 |
| Dibis 1 | SP | M | ME | 26 Apr 04 | 1 May | 8 |
| Dibis 2 | SP | M | ME | 26 Apr 04 | 1 May | 8 |
| Dibis 3 | SP | M | ME | 26 Apr 04 | 1 May | 8 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | 30 Apr | 8 |
| Doura 4 | CP | M | ME | 14 Apr 04 | 31 May | 20 |
| Doura 3 | CP | R | GRD/RIE | 1 Mar 03 | 15 May | 20 |
| Doura 3 | SP | M | ME | 18 Mar 04 | 18 May | 65 |
| Doura 4 | SP | M | ME | 2 Feb 04 | 30 Apr | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 20 Jun | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 20 Jul | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 12 May | 30 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 23 May | 100 |
| Khor Zubayr 2 | CP | R | GRD/RIE | 15 Mar 04 | 3 Jul | 50 |
| Mosil 7 | CP | M | ME | 24 Apr 04 | TBD | 15 |
| Mussaibe 2 | SP | M | ME | 28 Feb 04 | 28 Apr | 200 |
| Nassirya 1 | SP | M | ME | 30 Mar 04 | 15 May | 130 |
| New Mulla 6 | CP | R | GRD/RIE | 28 Mar 04 | 15 May | 30 |
| Old Mulla 1 | CP | M | ME | 17 Apr 04 | 15 May | 15 |
| Old Mulla 2 | CP | M | ME | 17 Apr 04 | 15 May | 15 |
| Old Mulla 8 | CP | M | ME | 17 Apr 04 | 23 Apr | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| South Baghdad 1 | SP | M (Awaiting parts) | ME | 12 Feb 04 | TBD | 30 |
| South Baghdad 2 | SP | M (Awaiting Parts) | ME | 12 Feb 04 | TBD | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 18 May | 20 |
| Taji 4 | CP | M | ME | 21 Apr 04 | 15 JUL | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 JUL | 15 |
| Taji 6 | CP | M | ME | 2 Apr 04 | 26 May | 15 |

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 129 towers complete/216req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | Complete | 246 towers complete/246 req’d |
| Hartha-Qut – Wasit | 400 | Sabotage | GRD/RIE |  | Complete | 23 Apr Operational |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | Complete | Operational |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | TBD | No contract awarded |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 15 Jun |  |
| Dibis/Erbil-Qara Qosh | 132 | New Line | GRD/RIE |  | 15 May | Construction ongoing |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 30 Jun | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 5 Jul | Assessment underway |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | 1 Jul | Assessment underway |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Old Amarah-Burzulgan | 132 | Looting | GRD-RIE |  | 25 Jun | Assessment underway |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

Distribution:

| Power transferred from North to Middle 940 MW. |  |
| --- | --- |
| Power transferred from South to Middle 230 MW. |  |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW |
| Baghdad | 1350 | 29940 | 1248 | 1439 |
| Duhok | 80 | 1918 | 80 | 105 |
| Naynawa | 385 | 8019 | 334 | 488 |
| Tamim | 145 | 3221 | 134 | 175 |
| Salah Aldeen | 210 | 4880 | 203 | 243 |
| Anbar | 210 | 4184 | 174 | 213 |
| Dyala | 100 | 2197 | 92 | 130 |
| Babil | 105 | 2251 | 94 | 138 |
| Kirbala | 102 | 2109 | 88 | 110 |
| Najaf | 115 | 2435 | 101 | 126 |
| Kadsya | 70 | 1508 | 63 | 84 |
| Wasit | 75 | 2111 | 88 | 114 |
| Muthana | 58 | 1358 | 57 | 75 |
| Nasirya | 130 | 2593 | 108 | 125 |
| Misan | 60 | 1306 | 54 | 80 |
| Basra | 300 | 6461 | 269 | 284 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil