## A-Steam Power Stations
Reporting Peak for 05 MAY 2004 / Report Date - 06 MAY 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 1 | 8 | [5 empty] | 8 | 24 | #2 DLL; #3 gen earth fault; #4 prog maint
Baiji | Fuel Oil | 6 | 2 |  | 140 |  |  |  | 105 | 245 | 500 | #1, #3 prog maint; #4 stopped at 0010 under excit; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3, #4 prog maint; #5, #6 rehab
South Baghdad | Fuel Oil | 6 | 3 |  |  |  | 30 | 30 | 25 | 85 | 200 | #1, #2, #3 prog maint
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 |  | 210 |  |  |  | 410 | 860 | #2 prog maint; #4 oil leak
Nassirya | Crude | 4 | 3 |  | 165 | 160 | 110 |  |  | 435 | 600 | #1 prog maint
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 88 |  |  | 88 | 160 | #5 thrust bearing prob
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 180 |  |  | 180 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1451 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 05 MAY 2004 / Report Date - 06 MAY 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 2 | 180 | 125 | Gas Oil |  | Musil Dam Main | 4 | 3 | 400 | 600
M. Baiji | 8 | 1 | 20 |  | Gas Oil |  | Musil Dam reg | 4 | 2 | 24 | 60 | 300
Quds | 2 | 2 | 109 | 160 | CO & GO |  | Musil Pumping | 2 |  |  | 0
Mosil | 12 | 7 | 115 | 150 | 28 | #1, #2 TF; #7 prog maint; #8 TF; #9 reverse power | Haditha Dam | 6 | 4 | 235 | 160 | 400
Dibis | 3 | 2 | 53 | 30 | 29 | #4 TF | Samarra | 3 | 3 | 45 | 55 | 590
Old Mulla | 12 | 7 | 99 | 128 | 480 | #1, #2 TF; #7 HET; #8 prog maint; #12 TF | Himrin | 2 | 2 | 35 | 21 | 135
New Mulla | 6 | 4 | 116 | 173 | 3.1 | #4 unstable load; #6 TF | Hindia | 4 | 4 | 5 | 5 | 120
Taji | 7 |  |  | 55 |  | #1, #2 NGPL; #3 TF; #4 NGPL; #5 HET; #6 prog maint; #7 TF | Kufa | 4 | 2 | 2 | 0 | 60
M. Taji | 2 |  |  | 18 | Gas Oil | #2 software |  |  | Total | 746 | 896
Daura | 4 |  |  | 30 |  | #1, #2 NGPL; #3 needs rehab; #4 prog maint | System Generation |  | 71247 | MWh
Hilla | 4 | 4 | 60 | 64 | 25 |  | Syrian Line Generation |  | 1377 | MWh
Najaf | 3 | 3 | 115 | 129 | 23 |  | Turkey Line Generation |  | 2027 | MWh
Khor | 4 | 3 | 131 | 80 | Natural Gas | #2 prog maint | Total Generation |  | 80078 | MWh
Shuaiba | 2 | 2 | 7 | 20 | Natural Gas |  | System Peak Load |  | 3377 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas |  | Syria Peak Load |  | 60 | MW
Petro | 4 |  |  | 0 | Natural Gas |  | Turkey Peak Load |  | 82 | MW
M. Dibis | 4 | 2 | 6 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 3 | 17 | 0 | Gas Oil |  | Total Peak Load |  | 3785 | MW
Hmam/Zafranya | 7 |  |  |  | Gas Oil |  | Baghdad Load |  | 1240 | MW
Diesel |  |  | 70 |  | Gas Oil
|  | Total | 1098 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 05 MAY 2004 / Report Date - 06 MAY 2004
Power transferred from North to Middle775 MW.
Power transferred from South to Middle 240 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1240 | 24885 | 1037 | 1400
Duhok | 82 | 1933 | 81 | 109
Naynawa | 295 | 6494 | 271 | 491
Tamim | 115 | 2909 | 121 | 181
Salah Aldeen | 191 | 4541 | 189 | 247
Anbar | 195 | 4214 | 176 | 233
Dyala | 90 | 1999 | 83 | 134
Babil | 90 | 2348 | 98 | 142
Kirbala | 80 | 1811 | 75 | 107
Najaf | 93 | 2126 | 89 | 128
Kadsya | 60 | 1405 | 59 | 86
Wasit | 87 | 1966 | 82 | 122
Muthana | 55 | 1230 | 51 | 76
Nasirya | 125 | 2533 | 106 | 128
Misan | 65 | 1349 | 56 | 82
Basra | 290 | 6549 | 273 | 317