Daily Power System Highlights for May 13, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Generation:

Peak Power 4071Mw, 83,348Mw hours, 7-day Avg. 3826Mw

Generators Returned to Service:   (0)

Generators Unscheduled Out of Service   (15)                                                             415 Mw

| PLANT | Type SP, CP, RP, HP | Fault | Mw |
| --- | --- | --- | --- |
| Baiji 3 | SP | Recirculation Fan bearing | 105 |
| Najebia 5 | SP | Thrust bearing problem | 80 |
| South Baghdad 5 | SP | Air Heater | 30 |
| Baiji Mobile, 4 | CP | Fuel Filters | 25 |
| Doura 1,2 | CP | No gas pressure | 40 |
| Mosil 1 | CP | Rotor Defect | 15 |
| Mosil 2 | CP | Reverse Power | 15 |
| Mosil 9 | CP | Reverse Power | 15 |
| Old Mulla 7 | CP | High exhaust temp | 15 |
| Taji 1,2,5 | CP | No gas pressure | 45 |
| M. Taji 1 | CP | Planned Outage | 15 |
| M. Taji 2 | CP | Software | 15 |

RED – Denotes out of service since last report

Generators Scheduled Out of Service   (29)                                                                       1336 Mw

| PLANT | Type SP/NG | Prog. Maintenance(M) / Rehab (R) | Maint. Org. | Date out-of -service | Est. In-service Date | Mw |
| --- | --- | --- | --- | --- | --- | --- |
| Baiji 1 | SP | M | Bechtel | 21 Mar 04 | 21 May | 100 |
| Dibis 3 | SP | M | ME | 26 Apr 04 | TBD | 8 |
| Dibis 4 | SP | M | ME | 15 Mar 04 | TBD | 8 |
| Baiji 2 | CP | M | ME | 11 May 04 | 18 May | 80 |
| Doura 4 | CP | M | ME | 14 Apr 04 | 31 May | 20 |
| Doura 3 | CP | R | ME | 1 Mar 03 | TBD | 20 |
| Doura 3 | SP | M | ME | 18 Mar 04 | 18 May | 65 |
| Doura 4 | SP | M | ME | 2 Feb 04 | TBD | 65 |
| Doura 5 | SP | R | Bechtel | Jul 03 | 20 Jun | 100 |
| Doura 6 | SP | R | Bechtel | Jul 03 | 20 Jul | 100 |
| Dibis 4 | CP | R | GRD/RIE | Sep 03 | 15 May | 30 |
| Hartha 1 | SP | M | ME | 22 Mar 04 | 23 May | 100 |
| Khor Zubayr 2 | CP | R | GRD/RIE | 15 Mar 04 | 3 Jul | 50 |
| Mosil 7 | CP | M | ME | 24 Apr 04 | 18 May | 15 |
| Mosil 8 | CP | R | GRD/RIE | 6 Feb 04 | 4 Jun | 15 |
| Mussaibe 2 | SP | M (Additional work) | ME | 28 Feb 04 | 20 May | 200 |
| Nassirya 1 | SP | M | ME | 30 Mar 04 | 21 May | 130 |
| New Mulla 6 | CP | R | GRD/RIE | 28 Mar 04 | 23 May | 30 |
| Old Mulla 1 | CP | M | ME | 17 Apr 04 | 15 May | 15 |
| Old Mulla 2 | CP | M | ME | 17 Apr 04 | 15 May | 15 |
| Old Mulla 8 | CP | M | ME | 17 Apr 04 | 12 May | 15 |
| Old Mulla 12 | CP | R | GRD/RIE | 1 Oct 03 | 15 May | 15 |
| South Baghdad 1 | SP | M (Awaiting parts) | ME | 12 Feb 04 | 21 May | 30 |
| South Baghdad 2 | SP | M (Awaiting Parts) | ME | 12 Feb 04 | 20 May | 30 |
| South Baghdad 3 | SP | R | ME | 18 Mar 04 | 6 Jun | 20 |
| Taji 3 | CP | R | GRD/RIE | 6 Feb 04 | 23 Jul | 15 |
| Taji 4 | CP | M | GRD/RIE | 21 Apr 04 | 15 JUL | 15 |
| Taji 7 | CP | R | GRD/RIE | 1 Oct 03 | 15 JUL | 15 |
| Taji 6 | CP | M | ME | 2 Apr 04 | 26 May | 15 |

New In-service date

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

CP:  COMBUSTION POWER

RP:  RECIPROCATING POWER

HP:  HYDRO POWER

Transmission:

| LINE | Kv | Fault | Maint. Org. | Date out-of -service | Est. In-service Date | Comments |
| --- | --- | --- | --- | --- | --- | --- |
| Nassiriya-Khor Zubayr | 400 | Sabotage | Bechtel |  | 26 May | 159 towers complete/216req’d |
| Haditha-Baghd West | 400 | Sabotage | GRD/RIE |  | Complete | 246 towers complete/246 req’d |
| Hartha-Qut Wasit | 400 | Sabotage | GRD/RIE |  | Complete | 23 Apr Operational |
| Baiji - Baghd West #1 | 400 | Sabotage | GRD/RIE |  | Complete | Operational |
| Baghd E.-Baghd S. #2 | 400 | New Line | GRD/RIE |  | Complete | 81 towers complete/81req’d |
| Haditha – Qaim | 400 | Sabotage | GRD-RIE |  | 28 Feb 05 | Start date 21 May 04 |
| Baiji – Haditha | 400 | Sabotage | Bechtel |  | TBD | No contract awarded |
| Diyala Connection | 400 | New Line | ME |  | 15 Jun | Foundations under construction |
| Dibis/Erbil-Qara Quosh | 132 | New Line | GRD/RIE |  | 1 Jun | Construction ongoing |
| Dibis to Old Kirkuk | 132 | Reconductor | GRD-RIE |  | 31 Jul | Bids for work under evaluation |
| Mosul – Mosul East | 132 | Sabotage | ME |  | TBD |  |
| Shuwaiba-Toba-Hamar | 132 | Sabotage | ME |  | Complete | 44 towers complete/44 req’d |
| Samediya – New Baghdad | 132 | Reconductor | GRD-RIE |  | 5 Jul | Assessment underway |
| Jazair to Yarmook | 132 | Reconductor | GRD-RIE |  | TBD | Assessment underway |
| Baghd West – Jamia | 132 | Sabotage | ME |  | TBD |  |
| Burzulgan-Old Amarah | 132 | Looting | GRD-RIE |  | 25 Jun | Assessment underway |
| Temim- Tuz | 132 | Sabotage | ME |  | TBD |  |
| Nejibiya – Hartha | 132 | Sabotage | ME |  | TBD |  |

Lines Returned to service:

Distribution:  No report today

| Power transferred from North to Middle 790 MW. |  |
| --- | --- |
| Power transferred from South to Middle 220 MW. |  |
| GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW |
| Baghdad | 1345 | 27196 | 1133 | 1579 |
| Duhok | 80 | 1838 | 77 | 112 |
| Naynawa | 340 | 6500 | 271 | 519 |
| Tamim | 140 | 2975 | 124 | 190 |
| Salah Aldeen | 220 | 4584 | 191 | 257 |
| Anbar | 200 | 4348 | 181 | 236 |
| Dyala | 85 | 1554 | 65 | 130 |
| Babil | 110 | 1997 | 83 | 139 |
| Kirbala | 85 | 1351 | 56 | 106 |
| Najaf | 95 | 1993 | 83 | 130 |
| Kadsya | 65 | 1224 | 51 | 91 |
| Wasit | 95 | 1620 | 68 | 121 |
| Muthana | 45 | 1205 | 50 | 73 |
| Nasirya | 110 | 2694 | 112 | 131 |
| Misan | 45 | 1367 | 57 | 81 |
| Basra | 330 | 7152 | 298 | 342 |

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil