## A-Steam Power Stations
Reporting Peak for 14 MAY 2004 / Report Date - 15 MAY 2004
A - Steam Power Stations
Power Stations | Type Fuel | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load MW | Remarks
|  |  |  | 1 | 2 | 3 | 4 | 5 | 6
Dibis | Natural Gas | 4 | 2 | 8 | 8 |  |  |  |  | 16 | 24 | #3 gen earth fault; #4 synch at 2120, stopped at 0026 DLL
Baiji | Fuel Oil | 6 | 4 |  | 125 | 100 | 75 |  | 95 | 395 | 500 | #1 prog maint; #3 synch at 1438; #5 forced outage
Daura | Fuel Oil | 4 | [7 empty] | 0 | 180 | #3, #4 prog maint; #5, #6 rehab
South Baghdad | Fuel Oil | 6 | 2 |  |  |  | 25 |  | 30 | 55 | 200 | #1, #2, #3 prog maint; #5 prog maint
Mussaibe | Crude and Fuel Oil | 4 | 3 | 205 |  | 200 | 250 |  |  | 655 | 860 | #2 prog maint
Nassirya | Crude | 4 | 3 |  | 160 | 160 | 130 |  |  | 450 | 600 | #1 prog maint
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 80 |  |  | 80 | 160 | #5 thrust bearing prob
Hartha | Natural Gas and Crude | 4 | 1 |  |  |  | 180 |  |  | 180 | 300 | #1 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1831 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Reporting Peak for 14 MAY 2004 / Report Date - 15 MAY 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 85 | 125 | GO+1+FO | #2 c. ch maint | Musil Dam Main | 4 | 3 | 490 | 600
M. Baiji | 8 | 3 | 60 |  | Gas Oil |  | Musil Dam reg | 4 | 2 | 26 | 60 | 300
Quds | 2 | 2 | 117 | 160 | CO & FO | 14 trucks | Musil Pumping | 2 |  |  | 0
Mosil | 12 | 7 | 115 | 150 | 28 | #1, #2 TF; #7 prog maint; #8 TF; #9 rotor defect | Haditha Dam | 6 | 4 | 310 | 160 | 500
Dibis | 3 | 2 | 49 | 30 | 29 | #4 TF | Samarra | 3 | 3 | 46 | 55 | 450
Old Mulla | 12 | 7 | 98 | 128 | 500 | #1, #2 TF; #4 load unbalanaced; #8 prog maint; #12 TF | Himrin | 2 | 2 | 36 | 21 | 135
New Mulla | 6 | 4 | 120 | 173 | 3.2 | #5 stopped at 0046 to connection; #6 TF | Hindia | 4 | 4 | 5 | 5
Taji | 7 |  |  | 55 |  | #1, #2 NGPL; #3, #4 TF; #5 NGPL; #6 prog maint; #7 TF | Kufa | 4 | 2 | 2 | 0
M. Taji | 2 |  |  | 18 | Gas Oil | #1, #2 TF |  |  | Total | 915 | 896
Daura | 4 |  |  | 30 |  | #1, #2 NGPL; #3 needs rehab; #4 prog maint | System Generation |  | 79988 | MWh
Hilla | 4 | 4 | 60 | 64 | 20 | #5 running during peak load | Syrian Line Generation |  | 1417 | MWh
Najaf | 3 | 3 | 65 | 129 | 19 |  | Turkey Line Generation |  | 1875 | MWh
Khor | 4 | 3 | 120 | 80 | Natural Gas | #2 prog maint | Total Generation |  | 88907 | MWh
Shuaiba | 2 | 2 | 5 | 20 | Natural Gas |  | System Peak Load |  | 3859 | MW
M. Shuaiba | 2 |  |  |  | Natural Gas | split with refinery | Syria Peak Load |  | 60 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Turkey Peak Load |  | 81 | MW
M. Dibis | 4 | 2 | 6 | 24 | Natural Gas |  | Fixed Gen Peak Load |  | 266 | MW
Mossil East | 5 | 2 | 12 | 0 | Gas Oil |  | Total Peak Load |  | 4266 | MW
Hmam/Zafranya | 7 | 1 | 2 |  | Gas Oil |  | Baghdad Load |  | 1475 | MW
Diesel |  |  | 74 |  | Gas Oil
|  | Total | 998 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Reporting Peak for 14 MAY 2004 / Report Date - 15 MAY 2004
Power transferred from North to Middle 750 MW.
Power transferred from South to Middle 210 MW.
GOVERNORATE | Peak Load MW | MWH | Average Load MW | Demand Load MW
Baghdad | 1475 | 27760 | 1157 | 1425
Duhok | 80 | 1924 | 80 | 112
Naynawa | 361 | 8562 | 357 | 515
Tamim | 155 | 3472 | 145 | 196
Salah Aldeen | 215 | 4993 | 208 | 251
Anbar | 185 | 4583 | 191 | 237
Dyala | 96 | 2453 | 103 | 140
Babil | 135 | 2498 | 104 | 144
Kirbala | 66 | 1680 | 70 | 110
Najaf | 125 | 2327 | 97 | 133
Kadsya | 55 | 1463 | 61 | 88
Wasit | 95 | 2132 | 89 | 121
Muthana | 55 | 1360 | 57 | 77
Nasirya | 105 | 2625 | 109 | 125
Misan | 75 | 1480 | 62 | 82
Basra | 290 | 7133 | 297 | 347