## A-Steam Power Stations
REPORT DATE -28 NOVEMBER 2003
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 2 | 0 | 0 | 8 | 8 |  |  | 16 | 24 | No. 2 FWP. No.1 loss of flame.
Baiji | Fuel Oil | 6 | 4 | 100 | 85 | 95 | 0 | 0 | 80 | 360 | 500 | No. 5 rehab. No. 4 stopped boiler leak 0934.
Dura | Fuel Oil | 4 | 1 |  |  | 75 | 0 | 0 | 0 | 75 | 180 | No. 4: Programmed Maintenance10 OCT to 25 NOV. Nos. 5 & 6: Rehabilitation.
South Baghdad | Fuel Oil | 6 | 1 | 0 | 0 | 30 | 0 | 0 | 0 | 30 | 200 | No. 6 programmed mnt 11 NOV to 26 DEC. No. 4 and 5 stopped boiler leak. No. 1 stopped 1251 fuel pump. No. 2 stopped 1133 fuel pump.
Mussaibe | Crude and Fuel Oil | 4 | 1 | 0 | 0 | 0 | 200 |  |  | 200 | 860 | No. 2 program mnt 20 OCT to 12 NOV prob in field breaker. No. 3 program mnt 5 NOV to 20 DEC. No. 1 tripped 0002 boiler leak.
Nassirya | Crude | 4 | 3 | 150 | 140 | 0 | 100 |  |  | 390 | 600 | No. 3 programmed mnt 11 NOV to 11 DEC. No. 4 expan.
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 0 | 90 |  | 90 | 160 | No. 4 programmed mnt 6 NOV to 21 DEC.
Hartha | Natural Gas and Crude | 4 | 1 | 150 |  |  | 0 |  |  | 150 | 300 | No. 4 Programmed Maintenance from 23 OCT to 23 DEC.
[9 empty] | Total: | 1311 | 2824

## B- Gas_C-Power Stations
Report Date- 28 NOVEMBER 2003
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 115 | 125 | Gas Oil | No. 1 s/b. | Musil Dam Main | 4 | 2 | 200 | 600
Quds | 2 | 2 | 80 | 160 | Gas Oil | 44 trucks. | Musil Dam reg | 4 | 3 | 35 | 60 | 450
Mosil | 12 | 7 | 105 | 150 | 16 | No. 1 rotor defect. No. 2 ACC. No. 8 program mnt. No. 3 control cards. No. 5 stopped at 2330. | Musil Pumping | 2 | 0 | 0 | 0
Dibis | 3 | 0 | 0 | 60 | 32 | No. 5 problem turbine rotor. No. 6: Programmed Maintenance. No. 4 rotor defect. | Haditha Dam | 6 | 2 | 120 | 160 | 300
Old Mulla | 12 | 7 | 88 | 128 | 20 | No. 1 gas control. No. 2 gen protec. No. 5 Programmed Mnt. No. 12 rehab. No. 6 gene. Prot. | Samarra | 3 | 3 | 51 | 55 | 475
New Mulla | 6 | 3 | 100 | 173 | 21 | No. 6 Generator Defective. No. 4 cooling fan. No. 3 prog. Mnt. | Himrin | 2 | 1 | 22 | 21 | 90
Taji | 7 | 5 | 80 | 55 | 13 | No. 5 Diesel. No.7 Rehabilitation. | Hindia | 4 | 4 | 5 | 5 | 140
M. Taji | 2 | 0 | 0 | 20 | 0 | NGPL | Kufa | 4 | 0 | 0 | 1
Dura | 4 | 1 | 12 | 30 | 15 | No.3 Rehabilitation. No. 1 control. No. 4 tripped at 0001 NGPL. |  |  | Total | 433 | 896
Hilla | 4 | 4 | 65 | 64 | 26 |  | System Generation |  | 65846 | MWh
Najaf | 3 | 3 | 120 | 129 | 24 |  | Syrian Line Generation |  | 0 | MWh
Khor | 4 | 1 | 40 | 80 | Natural Gas | No. 4: Rehabilitation. No. 2 tripped at 0507 over speed. No. 3 tripped at 0333. | Turkey Line Generation |  | 2061 | MWh
Shuaiba | 2 | 1 | 10 | 20 | Natural Gas | No. 1 Programmed Maintenance. | Total Generation |  | 67907 | MWh
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | System Peak Load |  | 3243 | MW
M. Dibis | 4 | 0 | 0 | 24 | Natural Gas |  | Syria Peak Load |  | 0 | MW
Mossil East | 5 | 0 | 0 | 15 | Gas Oil |  | Turkey Peak Load |  | 90 | MW
Hmam | 2 | 0 | 0 |  | Gas Oil |  | Fixed Gen Peak Load |  | 77 | MW
[7 empty] | Total Peak Load |  | 3410 | MW
|  | Total | 825 | 1233 |  |  | Baghdad Load |  | 1300 | MW
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
GOVERNORATE | Peak Load MW | MWH | Average Load MW | 28 NOVEMBER, 2003
Baghdad |  |  | #VALUE! | Power transferred from North to Middle 770 MW
Duhok |  |  | #VALUE!
Naynawa |  |  | #VALUE! | Power transferred from South to Middle 120 MW
Tamim |  |  | #VALUE!
Salah Aldeen |  |  | #VALUE!
Anbar |  |  | #VALUE!
Dyala |  |  | #VALUE!
Babil |  |  | #VALUE!
Kirbala |  |  | #VALUE!
Najaf |  |  | #VALUE!
Kadsya |  |  | #VALUE!
Wasit |  |  | #VALUE!
Muthana |  |  | #VALUE!
Nasirya |  |  | #VALUE!
Misan |  |  | #VALUE!
Basra |  |  | #VALUE!
0
No data provided for governorates.