## A-Steam Power Stations
REPORT DATE -8 NOVEMBER 2003
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 1 | 0 | 0 | 8 | 0 |  |  | 8 | 24 | No. 2 Boiler Leakage. No. 1 FWP. No. 4 oil pump.
Baiji | Fuel Oil | 6 | 4 | 95 | 100 | 80 | 0 | 0 | 85 | 360 | 500 | No. 5 rehab. No. 3 synch 0111. No. 4 tripped 0829 CV close.
Dura | Fuel Oil | 4 | 1 |  |  | 75 | 0 | 0 | 0 | 75 | 180 | No. 4: Programmed Maintenance10 OCT to 25 NOV. Nos. 5 & 6: Rehabilitation.
South Baghdad | Fuel Oil | 6 | 4 | 40 | 0 | 25 | 30 | 0 | 30 | 125 | 200 | No.2 Boiler Leakage. Nos. 4 synch 0650. No. 5 stopped at 2105 boiler leakage.
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 | 0 | 0 | 200 |  |  | 400 | 860 | No. 2 program mnt 20 OCT to 12 NOV. No. 3 program mnt 5 NOV to 20 DEC.
Nassirya | Crude | 4 | 3 | 150 | 0 | 170 | 100 |  |  | 420 | 600 | No. 4 limited due to vacuum. No. 2 stopped FWL.
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 0 | 75 |  | 75 | 160 | No. 4 programmed mnt 6 NOV to 21 DEC.
Hartha | Natural Gas and Crude | 4 | 1 | 150 |  |  | 0 |  |  | 150 | 300 | No. 1 synch at 0840. No. 4 Programmed Maintenance from 23 OCT to 23 DEC.
[9 empty] | Total: | 1613 | 2824

## B- Gas_C-Power Stations
Report Date- 8 NOVEMBER 2003
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 130 | 125 | Gas Oil | No. 2 synch at 2037 stopped at 2150 s/b. | Musil Dam Main | 4 | 2 | 280 | 600
Quds | 2 | 2 | 120 | 160 | Gas Oil | 44 trucks. | Musil Dam reg | 4 | 3 | 30 | 60 | 450
Mosil | 12 | 7 | 95 | 150 | 14 | No. 1 rotor defect. No. 2 ACC. No. 8 program mnt. No. 10 MVAR cont. No. 3 servo. | Musil Pumping | 2 | 0 | 0 | 0
Dibis | 3 | 0 | 0 | 60 | 26 | No. 5 problem turbine rotor. No. 6: Programmed Maintenance. No. 4 rotor defect. | Haditha Dam | 6 | 2 | 73 | 160 | 300
Old Mulla | 12 | 6 | 80 | 128 | 27 | No. 1 excitation. No. 2 Clutch. No. 5 programmed maintenance. No. 7 Oil Cooler. No. 11 Programmed Maintenance. No. 12 rehab. | Samarra | 3 | 3 | 58 | 55 | 540
New Mulla | 6 | 5 | 160 | 173 | 27 | No. 6 Generator Defective. | Himrin | 2 | 1 | 23 | 21 | 130
Taji | 7 | 4 | 70 | 55 | 15 | No. 1 synch at 1530. No. 5 Diesel. No.7 Rehabilitation. No. 4 trip servo. | Hindia | 4 | 4 | 6 | 5 | 130
M. Taji | 2 | 0 | 0 | 20 | 0 | NGPL | Kufa | 4 | 1 | 1 | 1
Dura | 4 | 0 | 0 | 30 | 0 | No.1 Control. No.3 Rehabilitation. No. 2 NGPL. No. 4 tripped at 2250 NGPL. |  |  | Total | 471 | 896
Hilla | 4 | 4 | 65 | 64 | 29 | No. 4 synch at 1351. | System Generation |  | 68350 | MWh
Najaf | 3 | 3 | 90 | 129 | 27 |  | Syrian Line Generation |  | 1304 | MWh
Khor | 4 | 3 | 110 | 80 | Natural Gas | No. 4: Rehabilitation. | Turkey Line Generation |  | 1733 | MWh
Shuaiba | 2 | 1 | 4 | 20 | Natural Gas | No. 1 Programmed Maintenance. | Total Generation |  | 71387 | MWh
Petro | 4 | 0 | 0 | 0 | Natural Gas |  | System Peak Load |  | 3702 | MW
M. Dibis | 4 | 0 | 0 | 24 | Natural Gas |  | Syria Peak Load |  | 70 | MW
Mossil East | 5 | 0 | 0 | 15 | Gas Oil |  | Turkey Peak Load |  | 80 | MW
Hmam | 2 | 0 | 0 |  | Gas Oil |  | Fixed Gen Peak Load |  | 77 | MW
[7 empty] | Total Peak Load |  | 3929 | MW
|  | Total | 924 | 1233 |  |  | Baghdad Load |  | 1265 | MW
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
GOVERNORATE | Peak Load MW | MWH | Average Load MW | 8 NOVEMBER, 2003
Baghdad | 1265 | 23522 | 980.0833 | Power transferred from North to Middle 730 MW
Duhok | 80 | 1884 | 78.5
Naynawa | 350 | 8007 | 333.625 | Power transferred from South to Middle 226 MW
Tamim | 125 | 3091 | 128.7917
Salah Aldeen | 210 | 4623 | 192.625
Anbar | 190 | 3741 | 155.875
Dyala | 95 | 2060 | 85.8333
Babil | 110 | 2323 | 96.7917
Kirbala | 70 | 1668 | 69.5
Najaf | 100 | 2353 | 98.0417
Kadsya | 68 | 1479 | 61.625
Wasit | 100 | 2103 | 87.625
Muthana | 70 | 1389 | 57.875
Nasirya | 125 | 2654 | 110.5833
Misan | 70 | 1496 | 62.3333
Basra | 300 | 5525 | 230.2083
3328