## A-Steam Power Stations
REPORT DATE - DECEMBER 2003
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 1 | 0 | 0 | 0 | 8 |  |  | 8 | 24 | No.1 mnt 10 DEC to 25 JAN. No. 3 tripped 1715 FWP. No. 2 FWP.
Baiji | Fuel Oil | 6 | 3 | 0 | 85 | 85 | 100 | 0 | 0 | 270 | 500 | No. 5 rehab. No. 6 mnt 5 DEC to 19 JAN. No. 1 tripped at 726 A/H.
Dura | Fuel Oil | 4 | 1 |  |  | 75 | 0 | 0 | 0 | 75 | 180 | No. 4 Mnt 10 OCT to 12 DEC. Nos. 5 & 6: Rehabilitation.
South Baghdad | Fuel Oil | 6 | 1 | 35 | 0 | 0 | 0 | 0 | 0 | 35 | 200 | No. 6 mnt 11 NOV to 26 DEC. No. 5 mnt 1 DEC to 15 JAN. No. 2, 3 and 4 boiler leakage.
Mussaibe | Crude and Fuel Oil | 4 | 2 | 200 | 0 | 0 | 200 |  |  | 400 | 860 | No. 3 program mnt 3 NOV to 18 DEC. No. 2 problem in sealing.
Nassirya | Crude | 4 | 3 | 145 | 145 | 0 | 110 |  |  | 400 | 600 | No. 3 mnt 11 NOV to 11 DEC. No. 4 synch 1401 11 DEC.
Najebia | Natural Gas and Crude | 2 | 1 |  |  |  | 0 | 90 |  | 90 | 160 | No. 4 mnt 4 NOV to 22 DEC.
Hartha | Natural Gas and Crude | 4 | 1 | 150 |  |  | 0 |  |  | 150 | 300 | No. 4 Mnt from 23 OCT to 23 DEC.
[9 empty] | Total: | 1428 | 2824

## B- Gas_C-Power Stations
Report Date- 12 DECEMBER 2003
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 110 | 125 | Gas Oil |  | Musil Dam Main | 4 | 3 | 390 | 600
Quds | 2 | 1 | 112 | 160 | Gas Oil | 51 trucks. | Musil Dam reg | 4 | 3 | 35 | 60 | 450
Mosil | 12 | 7 | 115 | 150 | 33 | No. 1 rotor defect. No. 2 ACC. No.3 and 8 program mnt. | Musil Pumping | 2 | 0 | 0 | 0
Dibis | 3 | 0 | 0 | 60 | 26 | No. 4, 5& 6 rehab. | Haditha Dam | 6 | 2 | 150 | 160 | 400
Old Mulla | 12 | 8 | 120 | 128 | 510 | No. 1 gas control. No. 2 servo and C/B. No. 5 Programmed Mnt. No. 12 rehab. No. 6 tripped at 1920 HET. | Samarra | 3 | 2 | 41 | 55 | 410
New Mulla | 6 | 4 | 140 | 173 | 3.6 | No. 6 Generator Defective. No. 3 Mnt. | Himrin | 2 | 1 | 20 | 21 | 75
Taji | 7 | 2 | 33 | 55 | 20 | No. 5 flame. No.7 Rehabilitation. No. 2 mnt. No. 4 generator look out. No. 3 rotor. | Hindia | 4 | 4 | 4 | 5 | 85
M. Taji | 2 | 0 | 0 | 20 | 0 | No. 1 and 2 software. | Kufa | 4 | 0 | 0 | 1 | 0
Dura | 4 | 3 | 75 | 30 | 19 | No.3 Rehabilitation. |  |  | Total | 640 | 896
Hilla | 4 | 4 | 70 | 64 | 34 |  | System Generation |  | 71615 | MWh
Najaf | 3 | 2 | 98 | 129 | 32 | No. 2 program mnt. | Syrian Line Generation |  | 1248 | MWh
Khor | 4 | 2 | 110 | 80 | Natural Gas | No. 4: Rehabilitation. No. 1 VIB. | Turkey Line Generation |  | 601 | MWh
Shuaiba | 2 | 0 | 0 | 20 | Natural Gas | No. 1 oil leak. No 2 tripped 304 VIB. | Total Generation |  | 73464 | MWh
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | System Peak Load |  | 3266 | MW
M. Dibis | 4 | 0 | 0 | 24 | Natural Gas |  | Syria Peak Load |  | 20 | MW
Mossil East | 5 | 0 | 0 | 15 | Gas Oil |  | Turkey Peak Load |  | 30 | MW
Hmam | 2 | 0 | 0 |  | Gas Oil |  | Fixed Gen Peak Load |  | 77 | MW
[7 empty] | Total Peak Load |  | 3393 | MW
|  | Total | 993 | 1233 |  |  | Baghdad Load |  | 1350 | MW
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
GOVERNORATE | Peak Load MW | MWH | Average Load MW | 12 DECEMBER, 2003
Baghdad | 1350 |  | #VALUE! | Power transferred from North to Middle 700 MW.
Duhok | 30 |  | #VALUE!
Naynawa | 241 |  | #VALUE! | Power transferred from South to Middle 200 MW.
Tamim | 110 |  | #VALUE!
Salah Aldeen | 150 |  | #VALUE!
Anbar | 170 |  | #VALUE!
Dyala | 50 |  | #VALUE!
Babil | 78 |  | #VALUE!
Kirbala | 60 |  | #VALUE!
Najaf | 75 |  | #VALUE!
Kadsya | 50 |  | #VALUE!
Wasit | 75 |  | #VALUE!
Muthana | 45 |  | #VALUE!
Nasirya | 115 |  | #VALUE!
Misan | 60 |  | #VALUE!
Basra | 300 |  | #VALUE!
2959
MWH not provided by Ministry of Electricity