Power System Highlights for Saturday, December 27, 2003

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Contract signed with Turkey to purchase an additional 100 Mw of power. This additional power will bring the total from Turkey to 170 Mw.

Contract signed with General Electric to rehabilitate 5 generators at Mosul East.  Work scheduled to begin December 29, estimated duration of job 35 days.

Transmission Line Baghdad East – Kirkuk,, 400Kv line tripped, sabotage confirmed,  insulator  string damaged by gunfire, rain caused flashover and line trip. Climbing ladder bars removed from tower, which is in a remote location with difficult terrain. Loss of this link severely limits the network ability to transfer power from the North to the Center and Baghdad areas. Repair is in process but requires equipment to be taken in to the site.

Outage causing shortage of power in Central and Baghdad areas.

Generation:

- Daily System peak on 26 Dec – 3,307Mw.

- Daily system Demand on 26 Dec – 5,478 Mw (Estimated)

(3307, Actual Generation + 1880, Load Shed + 291, Corrected Frequency = 5478)

- Total generation – 75,493Mwh

- Imported power -  Power from Syria and Turkey included in System Peak

- Generators Returned to Service

- Generators Unscheduled Out of Service as of  26 DEC 03           817 Mw

Dibis 3 tripped due to feed water pump problem ---------------------------  8 Mw

Baiji 2 High bearing temperatures---------------------------------------------100 Mw

South Baghdad # 1,3,4 out due to boiler leaks ---------------------------- 75 Mw

Old Mulla 1 Gas Turbine - Gas control-----------------------------------------15 Mw

Old Mulla 2 Gas Turbine – Servo  and Circuit breaker problem --------15 Mw

Old Mulla 6 Gas Turbine Accessary Gear ----------------------------------- 15 Mw

Old Mulla 9 Synchronization ------------------------------------------------------15 Mw

New Mulla 4 Cooling Pump out---------------------------------------------------30 Mw

New Mulla 6 GT Assorted parts require replacement--------------------   30 Mw

Taji 4 GT Turbine problem ----------------------------------------------------     15 Mw

Taji 3 GT Compressor blades damaged-----------------------------------     15 Mw

Taji Mobile 1 and 2 software problem --------------------------------------     10 Mw

Baiji 2 GT oil leak -----------------------------------------------------------------  159 Mw

Mogul 1 GT Rotor defect ---------------------------------------------------------  15 Mw

Shuaiba 2 GT vibration trip at 0304 Dec 13 -----------------------------------10 Mw

Mussaibe 2 Seal, high pressure-------------------------------------------------200 Mw

Najebia 5, Lubricating oil leak ---------------------------------------------------- 90Mw

- Generators Scheduled Out of Service as of 26 DEC 03                        1317 Mw

- 3 Thermal units off-line for rehabilitation  ---------------------------------   285 Mw

  - Baiji 5 – 85 Mw -  ECD Jan 2004

  - Dora 5 and 6 – 200 Mw – ECD  May 2004

- 9 Thermal units in programmed maintenance --------------------------   778 Mw

  - Dibis 1 – 8 Mw –  ECD Jan 25

  - Baiji  6 -100 Mw –  ECD Jan 19

  - South Baghdad 5  35 Mw –  ECD Jan 15

  - South Baghdad 6  35 Mw –  ECD Dec 26

  - Old Mulla 5,7         30 Mw - TBD

  - Mussaibe 3          200 Mw – ECD Dec 21 (Not Complete yet)

  - Nassirya 3           130 Mw –  ECD Feb 04

  - Najebia 4                90 Mw – ECD Dec 22 (Not Complete yet)

  - Hartha 4               150 Mw – ECD Dec 23 (Not Complete yet)

- 7 Gas Turbine units off-line for rehabilitation ------------------------------129 Mw

  - Dibis 4, 5, 6       24 Mw

  - Old Mulla 12      15 Mw

  - Taji 7                 15 Mw

  - Doura 3             20 Mw

  - Khor Zubayr 4   55 Mw

- 5 units in programmed maintenance----------------- -----------------------125 Mw

  - Mosil 3                15 Mw

  - Old Mulla 5,7       30 Mw

  - New Mulla 3        30 Mw

  - Najaf 2                 50 Mw

Transmission:

Countrywide, Iraq’s electrical output continues to be constrained by damaged transmission and distribution lines. The lines have come down due to sabotage and bad weather.  Downed transmission lines increase the probability for complete nationwide blackout by reducing system contingency and causing mechanical damage at power plants. This may cause further temporary blackouts, which have already directly resulted in 1) impacted refineries causing reduced fuel flow to power plants and a subsequent reduction in power supply, and 2) damages in the power plants due to undercurrent causing units to come off-line for unscheduled maintenance.

- Transmission Lines out of service:

400KV

Haditha-Baghdad West –ECD slipped from Jan 24 to Feb 29

Haditha-Qarna – Wasit – ECD slipped from Jan 12 to Jan 24

Baghdad South – Qadisseya – ECD Jan 20

Baiji - Baghdad West #1 – ECD Jan 20

New line - Baghdad East-Baghdad South #2 – ECD Jan 23

Babil-Qadisiyah (collapsed towers/stolen conductors ECD 20 JAN)

Haditha – Qaim – no funding

Baiji – Haditha – no funding/no contractor

Baghdad East Autotransformer #4- need oil –finish 3 weeks after oil arrives

Baghdad East - Kirkuk, sabotage, No ECD reported

132KV

Mosul – Mosul East is sabotaged

Musalla – Rumala 132 Kv line still being sabotaged – 4 more towers down – now total of 7. This line ties the South generation to the North

Muthena GPS – Dour -  ECD Dec 28

Shuwaiba-Toba-Hamar– ECD Dec 30, delay due to material shortage

Baghdad West – Faluja, tripped No ECD

Omara-Burzegan – Sabotaged. ECD March 2004

Lines Returned to service:

None reported today