Power System Highlights for January 13, 2004

The CPA Electricity Advisor issues this report to note significant events or conditions of interest in the power sector.  The basic daily data on the power system is available on the CPA web site.

HIGHLIGHTS:

Power from Syria restored.

Generation:

- Daily System peak on 12 Jan – 3,596Mw.

- Daily system Demand on 12 Jan – 5,667 Mw (Estimated)

(3596 Actual Generation, + 1755 Load Shed, + 316 Corrected Frequency, = 5667)

- Total generation – 76,773Mwh

- Imported power -  Power from Syria (57Mw) and Turkey (82Mw) included in System Peak

- Generators Returned to Service                                                                         115 Mw

Mussaibe 2, SP                                                                                                       100 Mw

Old Mulla 6, NG, Accessory Gear                                                                              15Mw

Generators Unscheduled Out of Service as of 12 JAN 04                                          1098 Mw

| Dibis 4, SP, Steam Leak |  |  | 8 Mw |
| --- | --- | --- | --- |
| Baiji 5, SP, Forced Outage (No ECD) |  |  | 100 Mw |
| Baiji 3, SP, Thrust bearing defect |  |  | 100 Mw |
| Daura 4, Rotor |  |  | 100 Mw |
| South Baghdad 2, A/H |  |  | 30 Mw |
| *South Baghdad 4, Boiler leakage |  |  | 25Mw |
| Mussaibe 3, SP, Hydraulic test |  |  | 150Mw |
| *Najebia 4, shut down due to heavy rain |  |  | 35 Mw |
| *Najebia 5, shut down due to heavy rain |  |  | 90Mw |
| *Hartha 1, shut down due to heavy rain |  |  | 140Mw |
| Baiji 2, NG, Lubricating oil leak |  |  | 60 Mw |
| Mosil 1, NG, Rotor Defect |  |  | 15 Mw |
| Mosil 2, NG, Servo problem |  |  | 15 Mw |
| Mosil 9, NG, Rotor Defect |  |  | 15 Mw |
| Old Mulla 1,NG, Acc Gear |  |  | 15 Mw |
| Old Mulla 2, NG, Servo and Circuit breaker problem |  |  | 15 Mw |
| New Mulla 6, NG, Generator Defect |  |  | 30 Mw |
| Taji 3, NG, Compressor |  |  | 15 Mw |
| Taji 4, NG, Turbine problem |  |  | 15 Mw |
| *Daura 2, generator differential |  |  | 20Mw |
| Hilla,1,2,3,4, NG, Gas leak, caused low gas pressure |  |  | 80 Mw |
| Taji Mobile, 2, NG, Software problem |  |  | 10 Mw |
| Shuaiba 2, NG, Stand By |  |  | 5 Mw |
| *Petro 1, NG, shut down due to heavy rain |  |  | 10Mw |

* RED – Denotes out of service since last report

Generators Scheduled Out of Service as of 12 JAN  04                                        1009 Mw

- 2 Thermal units off-line for rehabilitation  ------------------------------------------------   200 Mw

  - Daura 5 and 6      200 Mw – ECD  May 2004

- 6 Thermal units in programmed maintenance -----------------------------------------   531 Mw

  - Dibis 1                      8 Mw – ECD Jan 25

  - Dibis 3                      8 Mw – ECD Feb15

  - Baiji  2                  100 Mw – ECD Mar 04

  - Baiji  6                  100 Mw – ECD Jan 19

  - South Baghdad 5   35 Mw – ECD Jan 15

  - Nassirya 4            130 Mw – ECD Jan 28

  - Hartha 4               150 Mw – ECD slipped to Jan 23

- 6 Gas Turbine units off-line for rehabilitation ---------------------------------------------123 Mw

  - Dibis 4, 5,              18 Mw

  - Old Mulla 12          15 Mw

  - Taji 7                     15 Mw

  - Daura 3                 20 Mw

  - Khor Zubayr 4       55 Mw

- 5 Gas Turbine units in programmed maintenance---------------------------------------155 Mw

  - Mosil 3 	       15 Mw

  - Old Mulla 5,7          30 Mw

  - New Mulla 4, 5       60 Mw (#5 ECD Mar 31)

  - Najaf 2        	       50 Mw (ECD Apr 30)

Transmission:

Countrywide, Iraq’s electrical output continues to be constrained by damaged transmission and distribution lines. The lines have come down due to sabotage and bad weather.  Downed transmission lines increase the probability for complete nationwide blackout by reducing system contingency and causing mechanical damage at power plants. This may cause further temporary blackouts, which have already directly resulted in 1) impacted refineries causing reduced fuel flow to power plants and a subsequent reduction in power supply, and 2) damages in the power plants due to undercurrent causing units to come off-line for unscheduled maintenance.

- Transmission Lines out of service:

400KV

Nassiriya-Khor Zubayr – ECD  May 1

Haditha-Baghdad West – ECD slipped from Jan 24 to Feb 29

Haditha-Qarna – Wasit – ECD slipped from Jan 12 to Jan 31

Baghdad South – Qadisseya – ECD Jan 20

Baiji - Baghdad West #1 – ECD Jan 24

New line - Baghdad East-Baghdad South #2 – ECD Jan 23

Haditha – Qaim – no funding

Baiji – Haditha – no funding/no contractor

Diyala Connection – ECD April 30

Baiji – Mosul – Line hit by helicopter 9 Jan, ECD, TBD

132KV

Mosul – Mosul East is sabotaged

Shuwaiba-Toba-Hamar– ECD Dec 30, (delay due to material shortage)

Baghdad West – Jamia – ECD TBD

Omara-Burzegan – Sabotaged. ECD March 2004

Temim- Tuz – ECD TBD

Nejibiya – Hartha  ECD TBD

Lines Returned to service:

None reported today

LEGEND OF ELECTRICAL SYSTEM POWER SOURCE

NG:  NATURAL GAS

SP:  STEAM POWER – These plants use either fuel oil or crude in burners

HYDRO:  WATER POWER

Data compiled and reported by:

LTC Tharnell M. Thomas

CENTCOM LNO CPA  Ministry of Electricity

thomast2orha.centcom.mil