## A-Steam Power Stations
REPORT DATE - 24 January 2004
A - Steam Power Stations
Power Stations | Type | No. of Units | No. of Operating Units | Units Load (MW) | [5 empty] | Total Load MW | Target Load | Remarks
| Fuel |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  | MW
Dibis | Natural Gas | 4 | 2 | 8 | 8 |  |  |  |  | 16 | 24 | #2 synch at 1110; #3 prog maint; #4 Boiler Leakage
Baiji | Fuel Oil | 6 | 3 | 90 |  | 80 | 75 |  |  | 245 | 500 | #2 Prog. Maint; #3 synch at 1649; #4 synch 1500; #5 forced outage; #6 prog maint
Daura | Fuel Oil | 4 | 1 |  |  | 75 |  |  |  | 75 | 180 | #4 rotor repair; #(5+6) Rehab
South Baghdad | Fuel Oil | 6 | 2 | 30 |  |  | 25 |  |  | 55 | 200 | #2 air heater defect; #3 stopped at 1625 boiler leakage; #4 synch 1500; #5 synch at 1555, stopped at 1650; #6 boiler leakage
Mussaibe | Crude and Fuel Oil | 4 | 4 | 200 | 80 | 150 | 210 |  |  | 640 | 860 | #2 limited to C.W. P; #3 boiler check
Nassirya | Crude | 4 | 3 | 140 | 140 | 145 |  |  |  | 425 | 600 | #4 prog maint. 28 DEC to 28 JAN.
Najebia | Natural Gas and Crude | 2 | 2 |  |  |  | 75 | 85 |  | 160 | 160
Hartha | Natural Gas and Crude | 4 | 1 | 140 | [5 empty] | 140 | 300 | #4 prog maint
| Out of Service for Unscheduled Maintanence | [7 empty] | Total: | 1756 | 2824
Out of Service for Program Maintanence/Rehab
No activity
Not Performing at Peak Performance

## B- Gas_C-Power Stations
Report Date- 24 January 2004
B- Gas Power Stations | [6 empty] | C -Hydro Power Stations
Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Fuel Use | Remarks | Power Stations | No. of Units | No. of Operating Units | Station Load | Target Load | Discharge m3/Sec
Gas Pressure
Baiji | 2 | 1 | 130 | 125 | Gas Oil | #2 lubricating oil leak from bearing | Musil Dam Main | 4 | 3 | 450 | 600
Quds | 2 | 2 | 125 | 160 | Gas Oil | 28 trucks; #2 limited to C.O. filter | Musil Dam reg | 4 | 4 | 47 | 60 | 650
Mosil | 12 | 8 | 123 | 150 | 27 | #1 rotor defect; #2 servo + ACC; #9 rotor defect; #11 stopped at 0021 11kv earth fault | Musil Pumping | 2 | 1 | 110 | 0
Dibis | 3 | 1 | 28 | 30 | 25 | #4 and #5 rehab | Haditha Dam | 6 | 2 | 140 | 160 | 250
Old Mulla | 12 | 7 | 93 | 128 | 410 | #1 ACC gear, #2 servo, #5 prog maint, #10 prog maint; #12 rehab | Samarra | 3 | 2 | 33 | 55 | 330
New Mulla | 6 | 4 | 130 | 173 | 3 | #4 prog maint; #6 Generator defect | Himrin | 2 | 1 | 23 | 21 | 90
Taji | 7 | 4 | 60 | 55 | 17 | #3 Compressor; #4 flame def; #7 Rehab. | Hindia | 4 | 4 | 5 | 5 | 110
M. Taji | 2 | 1 | 8 | 18 | 17 | #2 software. | Kufa | 4 | 0 | 0 | 0
Daura | 4 | 3 | 70 | 30 | 15 | #3 Rehab |  |  | Total | 808 | 896
Hilla | 4 | 4 | 70 | 64 | 20 | #1 synch at 1720 | System Generation |  | 75760 | MWh
Najaf | 3 | 2 | 95 | 129 | 20 | #2 prog maint | Syrian Line Generation |  | 1407 | MWh
Khor | 4 | 3 | 110 | 80 | Natural Gas | #3 synch at 1510; #4 Rehab | Turkey Line Generation |  | 1904 | MWh
Shuaiba | 2 | 1 | 8 | 20 | Natural Gas | #2 gas turbine check | Total Generation |  | 79071 | MWh
M. Shuaiba | 2 |  |  |  | Natural Gas | split with the refinery | System Peak Load |  | 3633 | MW
Petro | 4 | 1 | 10 | 0 | Natural Gas |  | Syria Peak Load |  | 60 | MW
M. Dibis | 4 | 2 | 6 | 24 | Natural Gas |  | Turkey Peak Load |  | 82 | MW
Mossil East | 5 | 2 | 12 | 0 | Gas Oil |  | Fixed Gen Peak Load |  | 127 | MW
Hmam/Zafranya | 7 | 2 | 3 |  | Gas Oil |  | Total Peak Load |  | 3902 | MW
Diesel |  |  | 14 |  | Gas Oil |  | Baghdad Load |  | 1350 | MW
|  | Total | 1095 | 1186
Notes: Prepared from data submitted by D.G. Mohsin T. Hassan (1 (914) 360 6590).
Edited by Electricity Commission U.S. Advisor Staff.

## Peak Loads
Report Date - 24 January 2004
GOVERNORATE | Peak Load MW | MWH | Average Load MW
Power transferred from North to Middle 550 MW.
Power transferred from South to Middle 60 MW.
Baghdad | 1350 | 27735 | 1156
Duhok | 82 | 1862 | 78
Naynawa | 421 | 9629 | 401
Tamim | 141 | 3547 | 148
Salah Aldeen | 200 | 4407 | 184
Anbar | 185 | 4101 | 171
Dyala | 81 | 1918 | 80
Babil | 100 | 2266 | 94
Kirbala | 95 | 2203 | 92
Najaf | 100 | 2530 | 105
Kadsya | 55 | 1416 | 59
Wasit | 85 | 1895 | 79
Muthana | 55 | 1347 | 56
Nasirya | 115 | 2574 | 107
Misan | 65 | 1411 | 59
Basra | 350 | 7740 | 323